## Slide 1
Lesson 10
Chapter 14
DC Motors
Sections
14.1 Introduction
14.2 DC motor operating principles
14.3 Types of DC motors
14.4 Losses and efficiency
14.5 DC motor control and protection
14.6 Other types of DC motors

## Slide 3
Chapter 14
DC motors

## Slide 4: About this chapter
DC motors and DC generators share much in common, as Gramme discovered in 1873, thereby paving the way for their development.
This chapter:
describes the operating principles and construction of various types of DC motors
describes how each type performs when providing power to a load.

## Slide 5: Contents
14.1 Introduction
14.2 DC motor operating principles
14.3 Types of DC motors
14.4 Losses and efficiency
14.5 DC motor control and protection
14.6 Other types of DC motors

## Slide 6
Lesson 10
Chapter 14
DC Motors
Sections
14.1 Introduction
14.2 DC motor operating principles
14.3 Types of DC motors
14.4 Losses and efficiency
14.5 DC motor control and protection
14.6 Other types of DC motors

## Slide 7: 14.1 Introduction
A DC motor converts electrical energy into mechanical energy – a DC generator in reverse.
DC motors are classified by how the main magnetic field is produced. This gives the same five types as for generators.
That is, permanent magnet and separately excited, and the three types of field coil connections used in self-excited generators: shunt, series and compound.

## Slide 8: Example DC motors
Examples of DC motors, two industrial types, one automotive
Notes: Figure 14.1

## Slide 9: 14.2 DC motor operating principles
A basic DC motor, where current flowing in the coil produces a magnetic field that interacts with the main field, causing the
loop to rotate
Notes: Figure 14.2

## Slide 10: Motor effect
The motor effect, which is caused by an electric current flowing in a coil that is free to rotate in a magnetic field
Notes: Figure 14.3

## Slide 11: Fleming’s rules
To find the direction of rotation of a motor, arrange the thumb and fingers of your left hand so they are at mutual right angles. The thumb points in the direction of the magnetic force acting on the conductor, and therefore its direction of rotation.
Notes: Figure 14.4

## Slide 12: Force and torque
The force acting on a current-carrying conductor depends on the strength of the magnetic field, the current in the conductor and the effective length of the conductor.
That is:
F = BlI
where:
F = force in newtons
B = flux density of the magnetic field in tesla
l = effective length of the conductor in metres
I = current flowing in conductor (amperes)

## Slide 13: Torque
Torque, or turning effort, is a force that produces rotational motion and is measured in newton metres (Nm).
If the force and the diameter of the armature are known, torque can be determined with the equation:
T = Fr
where:
T = torque in newton metres (Nm)
F = force in newtons
r = armature radius in metres (dia/2).

## Slide 14: Motor back-EMF
The induced voltage in a motor has the opposite polarity to the applied voltage, and therefore opposes the applied voltage
Notes: Figure 14.5

## Slide 15: Armature current
The voltage available to cause current to flow in the armature is the difference between the applied voltage (V) and the back-EMF (EG).
If the armature resistance is known, the armature current (IA) can be calculated with Ohm’s law.
That is:

## Slide 16
Armature current changes with load
Because the back-EMF is proportional to the speed of armature rotation, if the motor tends to slow down due to increased load, the back-EMF will reduce.
This allows more current to flow in the armature, thereby providing the extra power as torque needed to drive the increased load.

## Slide 17
Torque and armature current
The force producing torque is due to the interaction of the armature’s magnetic field and the main magnetic field.
If either field is increased in strength, the force between them will also increase.
Because the strength of the armature’s magnetic field is proportional to the armature current, torque is therefore proportional to magnetic field flux (Φ) and armature current (IA).

## Slide 18: Equation for torque
T = kΦIA
where:
T = torque in newton metres (Nm)
k = machine constant
Φ = main field flux in webers (Wb)
IA= armature current.
Machine constant is a given value that includes factors such as number of poles, how the armature is wound and the number of conductors.

## Slide 19: Power output
The mechanical output power of a DC motor can be calculated in two ways. The first uses an equation based on the machine’s mechanical performance, namely torque
and speed:
where:
Pout = output power in watts
n = speed in RPM
T = torque in newton metres.

## Slide 20: Power output – equation 2
The power output of a DC motor also approximately equals the product of the back-EMF (EG) and the armature
current (IA). This doesn’t take into account all the losses in the machine, but is often accurate enough.
That is:
Pout = EG × IA
where:
EG = armature generated voltage (volts)
IA = armature current (amps).

## Slide 21: Speed
The speed of a DC motor is directly proportional to its terminal voltage (V) and inversely proportional to the field flux (Φ).
This means there are two ways to increase the speed of motor:
1. increase the supply voltage
2. reduce the strength of the motor’s main magnetic field.

## Slide 22: Equation to find speed
where:
n = speed in revs per minute
Pout = output power in watts
T = torque in newton metres.

## Slide 23: Summing up
A DC motor has the same construction as a DC generator.
Use Fleming’s left-hand rule to find the direction of rotation of a motor when the direction of the current and magnetic flux are known.
When a DC motor is running, the armature produces a back-EMF that opposes the supply voltage. This limits the value of the armature current.

## Slide 24: Summing up (2)
When the load on a DC motor is increased, its speed and therefore its back-EMF reduce, causing the armature current to increase. This provides the additional torque to drive the increased load.
The back-EMF of a motor equals its terminal voltage minus the armature voltage drop (IARA).

## Slide 25: Summing up (3)
The speed of a DC motor is directly proportional to its terminal voltage and inversely proportional to the strength of the main magnetic field.
The output power of a DC motor is approximately equal to the product of its back-EMF and armature current.
Power also equals the product of torque and speed, divided by 9.55.

## Slide 26: 14.3 Types of DC motors
There are five basic types of DC motors:
permanent magnetic DC motor
separately excited DC motor
shunt DC motor
series DC motor
compound motor.
These have an identical construction to their equivalent as a generator and each type have certain characteristics that suit particular applications.

## Slide 27: Permanent magnet DC motor
DC permanent magnet motors come in a wide range of sizes and power ratings. The 375 W motor shown could be used to power an electric utility vehicle.
Notes: Figure 14.7

## Slide 28: Speed control
Because the magnetic field strength is fixed, the speed of a permanent magnet motor is adjusted by varying the armature current
Notes: Figure 14.8

## Slide 29: Torque and speed curves
Torque and speed characteristics for a permanent magnet motor
Notes: Figure 14.9

## Slide 30: Separately excited DC motor
The speed of a separately excited motor can be varied by changing field current, armature current, or a combination of both methods
Notes: Figure 14.10

## Slide 31: Shunt DC motor
A shunt DC motor has its field coils in parallel with the armature. Speed can be controlled with a rheostat that controls the field current.
Notes: Figure 14.11
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 32: Torque and speed curves
Torque and speed characteristics for a shunt connected DC motor
Notes: Figure 14.12

## Slide 33: Series DC motor
Two-pole series motor connections. The diverter rheostat in the circuit diagram controls the field current, but is not typically used.
Notes: Figure 14.13
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 34: Torque and speed curves
Torque and speed characteristics for a series motor
Notes: Figure 14.14

## Slide 35: Compound motor
A compound motor has shunt and series field coils
Notes: Figure 14.15
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 36: Torque and speed curves
Torque and speed characteristics for series, shunt and compound motors with identical values of full-load current and full-load torque
Notes: Figure 14.16

## Slide 37: Summing up
Permanent magnet motors produce a linear torque and have good speed regulation.
Separately excited DC motors require an external DC supply to provide the field current.
They have similar characteristics to the permanent magnet motor, with the advantage that their speed can be controlled by varying the field current.

## Slide 38: Summing up (2)
A shunt DC motor has good load-speed regulation, and its speed is readily controlled by varying the current in the shunt field coils.
If the field current is too low, the motor speed can become excessive.
The series motor has a high starting torque, but can reach a dangerously high speed if unloaded.

## Slide 39: Summing up (3)
A cumulatively compounded DC motor has series and shunt field coils connected so their magnetic fields add to each other.
The characteristics of the motor depend on the relative strength of the series and shunt fields.
Typically, a compound motor has a high starting torque due to the series windings, and an acceptable no-load speed due to the shunt coils.

## Slide 40: Summing up (4)
All DC motors exhibit maximum torque at start-up (zero speed).
A DC motor will run in reverse if the polarity of the field coils or the armature terminals are reversed, but not both.

## Slide 41: 14.4 Losses and efficiency
Losses in a DC motor cause the motor to heat up
Notes: Figure 14.17

## Slide 42: Efficiency
The efficiency of a DC motor is found in the same way as for a DC generator. That is, by dividing the power output (Pout) by the power input (Pin) .
Efficiency (symbol η) is expressed as a percentage:

## Slide 43: Efficiency curves
Efficiency of a DC motor compared to speed and torque
Notes: Figure 14.19

## Slide 44: 14.5 DC motor control and protection
Operating a large DC motor requires a means of starting it, controlling its speed and protecting it against various types of fault conditions.
Some situations also require the motor to be reversed, or to be stopped quickly.

## Slide 45: DC motor starter
Four position, three terminal motor starter
Notes: Figure 14.21

## Slide 46: Motor starter resistors
Starter resistors for large motors are designed to dissipate considerable heat
Notes: Figure 14.22

## Slide 47: Speed control
Motor speed control is typically achieved by varying the shunt field current with a rheostat
Notes: Figure 14.23

## Slide 48: Braking a DC motor
Methods of braking a large DC motor include:
mechanical braking
dynamic braking, where the motor becomes a generator and supplies current to a load, or returns power to the power source (regenerative)
plugging, in which the motor is connected to run in reverse.

## Slide 49: Reversing a DC motor
To reverse a permanent magnet DC motor, the only option is to reverse the polarity of the DC supply.
To reverse a DC motor, either reverse the armature connections or the field connections.

## Slide 50: Reversing a permanent magnet DC motor
A permanent magnet DC motor is reversed by changing the polarity of the DC supply
Notes: Figure 14.24

## Slide 51: Reversing a shunt DC motor
A shunt DC motor is reversed by changing the polarity of the supply voltage to either the armature or the field. This can usually be done at the motor’s terminal box.
Notes: Figure 14.25

## Slide 52: Reversing a series DC motor
A series DC motor can sometimes be reversed by changing links in the terminal box to reverse the direction of current in either the armature or the series field coils
Notes: Figure 14.26

## Slide 53: Reversing a compound motor
When reversing the direction of a compound motor, either reverse the armature connections, or both the series and shunt coil connections
Notes: Figure 14.27

## Slide 54: Armature reaction
In a motor, armature reaction causes the magnetic field to twist in the opposite direction to the direction of rotation
Notes: Figure 14.28

## Slide 55: Interpoles
Interpoles reduce the effects of armature reaction. They are in series with the armature.
Notes: Figure 14.29

## Slide 56: 14.6 Other types of DC motors
The DC motors described so far are based on traditional technology and are widely used in industry.
Small DC motors that rely on advanced technology are also widely used.
Some of these motors operate on different principles to traditional motors.

## Slide 57: Printed circuit motor
The printed circuit motor has an armature constructed by etching a complex winding pattern on printed circuit board
Notes: Figure 14.30

## Slide 58: Brushless motor
This type of motor has an electronic circuit that creates a rotating magnetic field in a series of field coils. The rotor is a permanent magnet.
Notes: Figure 14.31

## Slide 59: Stepper motor
A stepper motor is rated by the number of discrete steps it can achieve per revolution. The motor shown can step by 7.5º.
Notes: Figure 14.34

## Slide 60: Stepper motor principle
Sequence where four cycles of operation for a 2-pole stepper motor rotates it by 90º per cycle. Coils A to D are energised electronically.
Notes: Figure 14.35

## Slide 61: High resolution stepper
Stepper motor with a serrated magnet rotor that aligns with the serrations on each pole piece. Each step moves the rotor by one serration (1.8º for this motor).
Notes: Figure 14.36

## Slide 62: Chapter summary
The speed of a DC motor is directly proportional to its terminal voltage and inversely proportional to the strength of the main magnetic field.
The output power of a DC motor is approximately equal to the product of its back-EMF and armature current.
Output power also equals the product of torque and speed divided by 9.55.

## Slide 63: Chapter summary (2)
Permanent magnet and separately excited DC motors have a linear torque and good load-speed regulation.
A shunt DC motor has good load-speed regulation, a series DC motor has good starting torque. A compound motor combines both benefits.
A DC motor has resistive (I2R) losses, core losses (magnetic effects) and mechanical losses (friction, etc.).
Efficiency is highest when the constant losses equal the resistive losses.

## Slide 64: Chapter summary (3)
A DC motor takes a high starting current, which in large motors is limited by a motor starter to around 150 per cent of its full-load current.
A motor starter can be manual or automatic, and consists of resistors connected in series with the motor armature. As the motor gains speed, the starter progressively reduces the amount of series resistance.
The speed of a DC motor is usually controlled by varying the current in the shunt field coils.

## Slide 65: Chapter summary (4)
Methods to bring a large DC motor to a halt include applying a mechanical brake to its shaft, passing the motor’s generated current through a load (dynamic braking), injecting the generated current back to the supply (regenerative) and reversing the DC supply to reverse the motor (plugging).
A DC motor can only be reversed by changing the direction of current in either the field coils or the armature.

## Slide 66: Chapter summary (5)
Armature reaction causes the main magnetic field to distort and shift the magnetic neutral, causing sparking at the brushes and reduced efficiency.
The effects of armature reaction are reduced by adding interpoles between the main poles, or using compensating windings, which are embedded in the main field poles.
In both cases the coils are in series with the armature.

## Slide 67: Chapter summary (6)
Other types of DC motors include the printed circuit motor, brushless motor, stepper motor and servomotor.
The armature in a printed circuit motor (pancake motor) is made by chemically etching a fibreglass disc laminated on both sides with copper.
A brushless motor has an electronic circuit that switches power to coils in the stator to create a rotating magnetic field that the magnetised rotor follows.

## Slide 68: Chapter summary (7)
A stepper motor rotates by a certain angle each time the control electronics receives an electrical pulse. This type of motor is used in positioning applications.
A servomotor is a type of permanent magnet motor designed to rapidly accelerate and decelerate.
A DC tachometer is a permanent magnet motor acting as a generator, where the output voltage is proportional to the shaft speed.