## Slide 1
Lesson 8
Chapter 13
DC Generators
Part 2
Sections
13.1 Introduction
13.2 DC generator operating principles
13.3 DC machine construction
13.4 Separately excited DC generator

## Slide 3
Chapter 13
DC Generators

## Slide 4: About this chapter
Although Faraday discovered the principles of electromagnetic induction in 1831, it took 40 years before a commercially viable DC generator was developed.
This chapter:
describes the operating principles and construction of various types of DC generators
looks at how each type of generator performs when providing power to a load
looks at applications and limitations of each generator.

## Slide 5: Contents
13.1 Introduction
13.2 DC generator operating principles
13.3 DC machine construction
13.4 Separately excited DC generator
13.5 Self-excited generators
13.6 Calculations

## Slide 6
Lesson 8
Chapter 13
DC Generators
Sections
13.1 Introduction
13.2 DC generator operating principles
13.3 DC machine construction
13.4 Separately excited DC generator

## Slide 7: 13.1 Introduction
A DC generator and a DC motor have a similar construction and are called DC machines.
A DC generator converts mechanical energy into electrical energy. The mechanical energy is from a prime mover that rotates the generator shaft.
Prime movers include diesel or petrol engines, hydro-power, steam turbines, etc.
The amount of electrical power produced depends on the power of the prime mover and design of the DC generator.

## Slide 8: Example DC generator
A 12.5 kW DC generator set, powered by a diesel prime mover
Notes: Figure 13.1
Courtesy of Fischer Panda GmbH

## Slide 9: 13.2 DC generator operating principles
A rotating magnet arranged to induce a current in a stationary coil. This arrangement produces an alternating current.
Notes: Figure 13.2

## Slide 10: Fixed magnetic field, rotating coil
A rotating coil inside a stationary magnetic field. The coil is connected to the load through brushes rubbing against sliprings. This device also produces an alternating current.
Notes: Figure 13.3

## Slide 11: Basic alternator
When a coil rotates in a magnetic field, the voltage induced in the coil changes polarity
Notes: Figure 13.4

## Slide 12: Basic generator
The commutator switches the coil connections every half turn. This causes the load current to always flow in the same direction.
Notes: Figure 13.5

## Slide 13: 13.3 DC machine construction
A DC machine has stationary parts built into a frame, and a rotary part called the armature.
Coils are wound on pole pieces that are attached to the frame. Pole pieces are made from steel laminations.
When supplied with an electric current, the pole pieces become magnetised.
Some machines have four or six poles, with the coil around each pole piece connected to give the opposite magnetic polarity to its two adjacent poles.

## Slide 14: Stator parts
Basic construction of the frame of a DC machine. The frame, pole pieces and coils provide the magnetic field.
Notes: Figure 13.6
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 15: Armature
An armature core is made of steel laminations, which are shaped to provide slots for the windings
Notes: Figure 13.7
Armature core and shaft from Multi-Amp Inst Basic Electricity for Electricians 1e, © 1992 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 16
Brushes – large machines
Brushes and brush gear for large machines
Notes: Figure 13.8

## Slide 17
Brushes – small machines
Brushes and brush gear for small machines, in this case for a four-pole machine
Notes: Figure 13.9

## Slide 18: Armature windings
Because there are two coils rather than a single coil, a smoother output voltage is obtained. The commutator now has four segments.
Notes: Figure 13.10

## Slide 19: Lap and wave windings
The two main types of armature windings are lap windings and wave windings.
A lap winding has the start and end of each coil connected to adjacent commutator segments.
In a wave winding, the ends of each coil are connected to segments some distance apart.

## Slide 20: Lap winding
Lap winding, in which each coil connects to adjacent commutator segments.
Notes: Figure 13.11

## Slide 21: Lap winding schematic
Schematic diagram of the illustration on the previous slide
Notes: Figure 13.12

## Slide 22: Wave winding
Wave winding, in which each coil connects to commutator segments some distance apart
Notes: Figure 13.13

## Slide 23: Comparison of winding types
A wave winding has two parallel paths between brush connections, with windings effectively in series.
This means a larger number of conductors contribute to output voltage, but because they’re in series, output current is less than from a lap wound armature.
A lap winding produces a lower voltage and a higher current than a wave winding.
Both types of armature windings produce the same amount of output power.

## Slide 24: 13.4 Separately excited DC generator
The magnetic field current in a separately excited DC generator is provided by an external DC supply.
The DC supply can be adjustable, or for a fixed supply voltage, connected in series with a variable resistance to control the value of the field current.
The DC supply can be from another DC generator mechanically connected to the main DC generator shaft.

## Slide 25: Example
A basic two-pole separately excited DC generator
Notes: Figure 13.14
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 26: Circuit diagram
Circuit diagram of a separately excited DC generator. The field rheostat adjusts the value of the field current.
Notes: Figure 13.15

## Slide 27: Equivalent circuit
Equivalent circuit of a separately excited DC generator. Coils are shown as DC resistances, the voltage produced by the armature is EG.
Notes: Figure 13.16

## Slide 28: Open-circuit characteristics
When there is no load connected to a generator, its terminal voltage (VT) will equal the EMF generated in the armature (EG). The value of this voltage depends on:
1. strength of the magnetic field created by the field coils
2. number of armature conductors connected in series, which depends on the construction of the armature and how it is wound
3. relative speed between the moving conductors and the magnetic field.

## Slide 29: Equation to find EG
where:
EG = voltage generated by the armature
p = number of poles
Φ = flux per pole in webers
n = revolutions per minute (RPM)
Z = number of effective armature conductors
a = number of parallel paths in the armature.

## Slide 30: Test setup
Circuit when determining a DC generator’s open-circuit characteristic, in which the speed is held constant for different values of field current while the output voltage is measured
Notes: Figure 13.17

## Slide 31: Output versus increasing field current
The open-circuit voltage curve of a DC generator is the same as the magnetisation (B–H) curve of the machine’s magnetic circuit
Notes: Figure 13.18

## Slide 32: Output versus increasing RPM
Voltage versus speed curve for a DC generator on no load
Notes: Figure 13.19

## Slide 33: Load characteristics
A DC generator is used to provide electrical power to a load.
It’s therefore useful to know how the generator performs under load conditions.
This is done with a load test in which the generator is run at its rated speed and field current while the load current is varied.

## Slide 34: Test setup
Load test circuit diagram, in which the generator’s terminal voltage is measured at different values of load current, for constant RPM and field current
Notes: Figure 13.20

## Slide 35: Load characteristic curve
The output voltage falls as the load is increased due to armature and brush resistance, and because of armature reaction
Notes: Figure 13.21

## Slide 36: Armature reaction
Armature reaction causes the machine’s magnetic field to twist in the direction of rotation
Notes: Figure 13.22

## Slide 37: Effects of armature reaction
Armature reaction causes:
flux to concentrate at the trailing pole tips and reduce at the leading pole tips
the magnetic flux to be distributed unevenly. As a result, the magnetic circuit in the machine is not being used effectively, and the generated voltage is reduced
sparking at the brushes, which can be reduced by moving the brushes to a new position.

## Slide 38: Brush position
Brushes are positioned so switching between commutator segments occurs at the magnetic neutral zone, when there is no induced current in the coils being switched
Notes: Figure 13.23

## Slide 39: Interpoles
Interpoles reduce the effects of armature reaction and are connected in series with the armature
Notes: Figure 13.24
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 40: 13.5 Self-excited generators
Most DC generators are self-excited, which means they provide their own field current.
There are various ways this can be done, and each method is named after the manner in which the field coils are connected.
They can be:
in series with the armature
in parallel (shunt)
a combination of both.

## Slide 41: Shunt generator
A shunt-connected DC generator has its field winding in parallel with the armature and (therefore) the output terminals
Notes: Figure 13.25
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 42: Load characteristic
The terminal voltage of a shunt DC generator falls dramatically under overload conditions, shown by the red section of the curve
Notes: Figure 13.26

## Slide 43: Voltage–speed characteristic
The voltage produced by a shunt generator varies almost proportionally to its speed of rotation, once the critical speed is reached.
Below this speed, the voltage produced by the generator is due mainly to its residual magnetism.
Notes: Figure 13.27

## Slide 44: Series generator
The field coils in a series DC generator are wound with few turns of heavy gauge wire, and are connected in series with the armature
Notes: Figure 13.28
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 45: Load characteristic
The terminal voltage of a series DC generator increases as the load current increases
Notes: Figure 13.29

## Slide 46: Voltage–speed characteristic
The voltage produced by a series generator varies almost proportionally to its speed of rotation
Notes: Figure 13.30

## Slide 47: Compound generator
The compound generator has two separate windings in each field coil, a series-connected coil and a shunt-connected coil
Notes: Figure 13.31
Adapted from Herman, Standard Textbook of Electricity 1e, © 1993 Delmar Learning, a part of Cengage Learning, Inc, reproduced by permission, www.cengage.com/permissions

## Slide 48: Circuit diagrams
Two ways of connecting the shunt field coils in a
compound generator
Notes: Figure 13.32

## Slide 49: Types of compound generator
Level-compound – the number of turns in the series coils keeps the generator’s terminal voltage almost constant from no load to full load.
Over-compound – has more turns in the series coils, causing the loaded voltage to rise above its no-load value.
Under-compound – has less turns in the series coils, causing the terminal voltage to fall under load.
Differential compound – in which the series coils oppose the magnetic field.

## Slide 50: Types of compound generator (2)
Curves showing how the output voltage of different types of compound generators behave under load
Notes: Figure 13.33

## Slide 51: 13.6 Calculations
In a typical installation, the load is connected to a DC generator with cables, which will have some value of resistance. Brushes and armature windings also have resistance.
The voltage drops across the cables and brushes-armature can be calculated if their resistance and the load current is known.
The armature’s generated EMF at full load can also be determined.

## Slide 52: 13.6 Calculations (2)
Shunt generator connected to a 400 V, 40 kW load. Brush and armature resistance is 0.08 Ω, total cable resistance is 0.1 Ω.
Notes: Figure 13.34

## Slide 53: Voltage drops due to resistance
To determine the voltage drops:
1. Find the load current, assuming the voltage across the load is 400 V.
Answer: IL = 100 A
2. Find the voltage at the generator terminals (VT) when the load current is 100 A and the load voltage is 400 V.
Answer: VT = 410 V

## Slide 54: Voltage drops due to resistance (2)
To determine the voltage drops:
3. Find the armature’s generated EMF (EG), assuming the only losses are due to the armature and brush resistance.
Answer: EG = 418 V

## Slide 55: Voltage regulation
Generators are rated at their full-load output voltage. Voltage regulation is the difference between the no-load and full-load voltages, divided by the full-load value. The answer is multiplied by 100 to express it as a percentage.
That is:
where:
VNL = no-load voltage
VFL = full-load voltage.

## Slide 56: Power loss and efficiency
Power losses include copper losses (I2R losses), mechanical losses due to friction and wind resistance, and magnetic core losses due to hysteresis, magnetic fringing and leakage, and eddy currents induced in the core.
Therefore, the prime mover driving a DC generator has to provide sufficient power to overcome all these losses.

## Slide 57: Efficiency
The ratio of the power output (Pout) and the power input (Pin) gives a measure of a machine’s efficiency.
Efficiency (symbol η) is expressed as a percentage.
That is:

## Slide 58: Chapter summary
DC machines (motors and generators) have virtually the same construction.
The frame and pole pieces in a generator provide a path for the magnetic field created by its field coils.
This field interacts with the rotating armature to induce a voltage in the armature coils.
The alternating armature current is converted by the commutator to direct current in the load.

## Slide 59: Chapter summary (2)
A lap wound armature has many parallel paths and suits a high current, low voltage machine.
A wave wound armature has two parallel paths and suits a high voltage, low current machine.
The magnetic field in a generator can be produced by permanent magnets (smaller machines), or field coils supplied by either an external DC source, or by the generator itself.

## Slide 60: Chapter summary (3)
Self-excited generators can be: shunt, where the field coils are in parallel with the armature; series, in which the armature current flows in the field coils; and compound, which combines shunt and series field coils.
Generators are rated by their output current at a rated output voltage, and have a specific direction of rotation. If the direction of rotation is reversed, a self-excited machine cancels its residual magnetism and cannot produce an output voltage.

## Slide 61: Chapter summary (4)
The mechanical energy required to drive a generator is proportional to, but greater than, the electrical energy being delivered by the generator.
A DC generator has resistive (I2R) losses, core losses (magnetic effects) and mechanical losses (friction, etc.).
Resistive losses are those due to any resistance in series with the armature’s generated EMF (EG) and the output terminals of the generator.

## Slide 62: Chapter summary (5)
DC machines (motors and generators) operate at a certain efficiency, which is the ratio of the power delivered by the machine (Pout) and the power required to drive the machine (Pin).
The % voltage regulation of a DC generator is a measure of how much its output voltage drops under load.

## Slide 63: Chapter summary (6)
A prime mover driving a DC generator has to overcome the opposing magnetic fields created by the armature and the generator’s main field.
The armature field strength increases with load current, requiring more mechanical power from the prime mover.