## Slide 1
Lesson 12
Chapter 22
Three Phase Motors
Sections
22.4 Motor protection

## Slide 2: 22.4 Motor protection
Motor protection and isolation requirements are specified by AS/NZS 3000:2007 in section 4.13.
In general, motor protection covers overload, overheating, over-temperature and where required, protection against restarting or reversal of rotation.
Isolation includes starting and stopping a motor with correctly rated devices.

## Slide 3: Motor starters
Starting currents can be many times the rated current, although the value quickly drops as the motor accelerates.
AS/NZS 3000 gives a guide to determining the value of a motor’s starting current, in the absence of manufacturer data, as being eight times the rated current of the motor.
Supply authorities impose limits on motor starting currents, although the limits depend on the authority.

## Slide 4: DOL motor starter
A direct-on-line motor starter is usually a contactor with a rating to suit the motor
Notes: Figure 22.31

## Slide 5: Contactor symbol
Circuit symbol for a three-phase contactor
Notes: Figure 22.32

## Slide 6: Thermal overload units
A thermal overload is adjusted to operate when the motor load current exceeds a certain value
Notes: Figure 22.33

## Slide 7: Circuit diagram
Circuit diagram of a DOL three-phase motor starter with thermal overload (TOL) protection
Notes: Figure 22.34

## Slide 8: Thermal overload relay
Operating principle of a thermal overload relay:a bimetallic strip is heated by a resistive heating element carrying the motor current
Notes: Figure 22.35

## Slide 9: Magnetic overload relay
Operating principle of a time delay magnetic overload relay: a piston attached to the solenoid plunger is slowed by travelling in an
oil-filled dashpot
Notes: Figure 22.36

## Slide 10: Fuses
High rupturing capacity (HRC) fuses have the element enclosed in a ceramic tube filled with powered silica.
This ensures rapid heating of the fusible element, arc quenching and containment of the energy.
Notes: Figure 22.37

## Slide 11: Circuit breakers
Circuit breakers incorporate an on-off switch as well as in-built overload protection.
They operate like a thermal or magnetic overload unit.
An overload condition operates the switch mechanism.
Notes: Figure 22.38

## Slide 12: Over-temperature protection
AS/NZS 3000 requires that an over-temperature device be fitted to unattended motors above a certain rating.
A motor can become hot due to overload or external conditions, such as hot weather.
This can mean a thermal overload unit will not always operate, as it senses an overload current, not the temperature of the motor.

## Slide 13: Embedded thermistors
Thermistors embedded in motor windings have a positive temperature coefficient (PTC) in which the thermistor resistance increases quickly after the reference temperature is reached
Notes: Figure 22.39

## Slide 14: Adverse environments
Motors designed to operate in hot, humid, wet or dusty environments have an IP Code rating (ingress protection rating).
The code is stamped on the motor nameplate, and consists of the letters IP followed by two digits.

## Slide 15: IP code
The first digit rates the level of protection the motor enclosure provides against access to live or moving parts, and the ingress of dust or other foreign bodies. Numbers range from 0 (no protection) to 6, which is dust tight.
The second digit refers to the level of protection a motor enclosure provides against the ingress of water. The numbers range from 0 (no protection) to 8, in which the motor can be fully and continuously immersed in water.

## Slide 16: TEFC motor
The totally enclosed, fan cooled motor (TEFC) is the most common type.
It has a fan fitted externally on the non-drive end of the shaft.
The fan draws air over the motor fins, removing excess heat and cooling the motor.
Notes: Figure 22.40

## Slide 17: ODP motor
An open drip proof (ODP) motor typically has a protection rating of IP22 or IP23.
It has vent openings in the end plates and an internal fan to blow air over the motor parts.
Water cannot be sprayed onto the end plates.
Notes: Figure 22.41

## Slide 18: TENV motor
A totally enclosed non-ventilated (TENV) motor, does not have a fan and relies on convection cooling.
Typically rated at IP55, they have V-ring seals between casing parts to maintain a good seal.
High temperature insulation is often used, as the motor is designed to run hot.
Notes: Figure 22.42

## Slide 19: XPRF motor
An explosion proof (XPRF) motor is used in hazardous environments.
This type of motor is designed to prevent it igniting surrounding materials, liquids or gases in the event the motor has an internal explosion, sparking or breakdown.
Notes: Figure 22.43

## Slide 20: Starting and reversing
The number of start-stop cycles allowed per hour depends on the motor design.
A typical three-phase 1 kW motor might be able to do this 10 to 15 times an hour.
A large motor (25 kW or more) would be limited to less than five starts an hour.
Each start-stop or forward-reverse cycle also causes wear on switching contacts.

## Slide 21: Reduced voltage motor starters
Block diagram of a reduced voltage motor starter. During starting, voltage to the motor is reduced to limit starting current and to reduce stress on the motor.
Notes: Figure 22.44

## Slide 22: Star–delta starter
The motor is started with its windings connected in star to reduce the voltage across each winding. At nearly full speed, the windings are connected in delta.
Notes: Figure 22.45

## Slide 23: Auto-transformer starter
This type of starter applies a reduced voltage to the motor using an auto-transformer
Notes: Figure 22.46

## Slide 24: Primary resistance starter
During start-up, KM1 is closed and KM2 open putting the motor in series with the resistors
Notes: Figure 22.47

## Slide 25: Summary
A DOL starter applies full voltage to a motor during start-up. This type of starter is permitted if the motor starting current does not exceed specified limits.
A DOL starter can be a switch, a contactor controlled by start and stop push-buttons, or a contactor controlled automatically by another circuit.
A contactor or switch controlling a motor should be rated at the motor’s starting current.

## Slide 26: Summary (2)
AS/NZS 3000 requires that all motors with a rating greater than 370 W be protected against overload.
Unattended motors above a certain rating must have over-temperature devices fitted to the motor (provisos apply).
A thermal overload relay senses the current taken by a motor and opens when the current exceeds the set value. These can be operated with a bimetallic strip or with a coil producing a magnetic field.

## Slide 27: Summary (3)
Fuses in a motor circuit must be capable of handling the motor starting current.
Motor start HRC fuses have a delay incorporated in the fusible element.
A miniature circuit breaker with thermal or magnetic (or both) overload protection is preferred over fuses, as all three phases of the supply are interrupted together under an overload condition.

## Slide 28: Summary (4)
Motor protection circuits often have a voltage relay to guard against an over or under voltage condition, which can cause a motor to overheat.
Over-temperature protection is often provided by thermistors embedded in the motor windings.
In a three-phase motor, the thermistors are connected to the motor control circuit.

## Slide 29: Summary (5)
Motors are rated to suit their operating environment and are given an ingress protection (IP) rating.
Motor enclosures range from the open drip proof type (ODP) to explosion proof (XRPF).
When the starting current of a motor is excessive, a reduced voltage starter is used.
These include the star–delta starter, electronic starter, auto-transformer starter and primary resistance starter.

## Slide 30: Equation summary
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles.

## Slide 31: Equation summary (2)
where:
s% = percentage slip
ns = synchronous speed
n = rotor speed.

## Slide 32: Equation summary (3)
where:
fr = rotor frequency
f = supply frequency.

## Slide 33: Equation summary (4)
where:
Pin = √3VLIL cos ϕ
new value of torque