## Slide 1
Lesson 17
Chapter 24
Synchronous Machines
Sections
24.2 Synchronous motors
24.3 Other types of synchronous motors

## Slide 2: 24.2 Synchronous motors
An alternator can operate as a synchronous motor.
There are two main categories of synchronous motors:
those that need an excitation source
those with a magnetised rotor that do not need external excitation, called non-excited motors.
These motors are generally rated at less than 1 kW, many types down to a only few watts.

## Slide 3: Examples of synchronous motors
The ship propulsion motor has a similar construction to an alternator, the smaller motors have a permanent magnet rotor
Notes: Figure 24.19

## Slide 4: Separately excited motor
Synchronous motor with a separate DC exciter
Notes: Figure 24.20

## Slide 5: Operating principle
When a three-phase supply is connected to the stator of a synchronous motor, a rotating field is set up in the stator that travels at synchronous speed.
Once the motor is running at its synchronous speed, it will remain at this speed regardless of load, unless the load increases to a point that causes the motor to loose synchronism.

## Slide 6: Starting methods
Methods of bringing a synchronous motor up to speed:
exciter as a motor: when the motor is at synchronous speed, its field is connected to the exciter, which is now a generator and no longer a motor
pony motor: once the motor is up to speed, AC power and DC excitation is applied to the synchronous motor
variable frequency drive (VFD): by setting the frequency of the drive system to a very low value and gradually increasing it.

## Slide 7: Induction motor start
Many synchronous motors have rotors fitted with ‘damping bars’, also called ‘amortisseur windings’.
In this type of rotor, an assembly like the squirrel cage in an induction motor is built into the pole faces of the rotor.
Synchronous motors with damping bars in the rotor can be started as an induction motor.

## Slide 8: Damping bars
3 MW synchronous motor rotor with amortisseur winding (damping bars), and the rotor laminations
Notes: Figure 24.21

## Slide 9: Loading the motor
At no-load, a synchronous motor rotor pole is central with the rotating stator field; when loaded, it lags the field by torque angle α. When overloaded, the magnetic coupling is lost and the motor stalls.
Notes: Figure 24.22

## Slide 10: Phasor diagrams
Effect of load on the line current in a synchronous motor.
α is the torque angle, and ϕ is the phase difference between the motor voltage and current.
Notes: Figure 24.23

## Slide 11: Varying the excitation current
Varying the excitation current varies the motor power factor.
Too little causes a lagging power factor.
Too much causes a leading power factor.
Notes: Figure 24.24

## Slide 12: V-curve
V-curves of a synchronous motor showing how power factor and motor current change with a change in field excitation current
Notes: Figure 24.25

## Slide 13: Hunting
When the load on a synchronous motor changes, the torque angle changes in a direction depending on whether the load has increased or decreased.
The change in torque angle has to occur against the inertia of the rotor, which means the rotor tends to swing around the point of equilibrium.
The average rotor speed remains constant, but with variations above and below synchronous speed. This effect is called hunting.

## Slide 14: Minimising hunting
Hunting can be reduced or prevented by increasing the excitation current to make the magnetic bond stronger.
Another technique is the use of damper bars fitted to the rotor.
The hunting effect induces a current in the bars, which by Lenz’s law will act to prevent the motion causing the induced current.
This dampens the swaying action of the rotor, and establishes smoother running.

## Slide 15: Reversing
A synchronous motor can be reversed by swapping any two phases supplying the stator.
This reverses the direction of the rotating field as in any three-phase motor.
If the motor is started with a pony motor or a DC exciter, its rotational direction will also have to be reversed.

## Slide 16: Stopping
A large synchronous motor has considerable inertia, and may take a while to stop rotating.
One method to stop the motor is dynamic braking, in which the motor becomes an alternator supplying current to either a short-circuit or load resistors.
Another method is mechanical braking with brake shoes around the motor shaft.

## Slide 17: Efficiency
The losses in a synchronous motor are similar to those in an alternator.
These include rotational losses such as bearing friction, windage and brush friction at the rotor slip rings, I2R losses in the stator and exciter windings, iron losses and losses due to the exciter.
As for all machines, efficiency:

## Slide 18: 24.3 Other types of synchronous motors
Other types of synchronous motors include:
Synchronous induction motors, which are similar in construction to the wound rotor induction motor.
Single-phase synchronous motors that include:
reluctance motors
hysteresis motors
permanent magnet motors.

## Slide 19: Summary
A synchronous motor runs at a fixed speed determined by the frequency of the supply and the number of poles in the motor.
Motors above 1 kW are excited by an external DC supply, smaller motors are non-excited and do not need a separate DC supply.
A synchronous motor is not normally self-starting. Once brought up to speed, it will lock into the rotating stator field and maintain synchronous speed.

## Slide 20: Summary (2)
Amortisseur windings, also called damping bars, are fitted to the rotor of a synchronous motor to prevent it hunting, and to also provide a means of starting the motor.
In this case, the bars allow the motor to start as an induction motor.
When the load on a synchronous motor is increased, the rotor speed remains constant, but the rotor shifts backwards by an amount called the torque angle.

## Slide 21: Summary (3)
The power factor of a synchronous motor depends on the level of DC excitation.
An under-excited motor has a lagging power factor, an over-excited motor has a leading power factor.
The optimum exciting current gives the minimum stator current for that load at unity power factor.

## Slide 22: Summary (4)
Because power factor can be determined by excitation, synchronous motors are sometimes used to improve power factor.
In this application, the motor is a synchronous capacitor.
Small synchronous motors are non-excited and some types have a permanent magnet rotor.

## Slide 23: Summary of equations
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles.
or

## Slide 24: Summary of equations (2)
where:
= alternator phase voltage
N = number of armature turns per phase
f = frequency of the generated voltage (Hz)
 = magnetic flux per pole in webers
k = machine constant.

## Slide 25: Summary of equations (3)
Apparent power:
S = VI (single-phase alternator)
S = √3VLIL (three-phase alternator).

## Slide 26: Summary of equations (4)
where:
= no-load voltage
= full-load voltage.

## Slide 27: Summary of equations (5)
where:
Pin = Pout + losses