## Slide 1
Lesson 16
Chapter 24
Synchronous Machines
Sections
24.1 Alternators

## Slide 3
Chapter 24
Synchronous machines

## Slide 4: About this chapter
Synchronous machines run at a speed that locks to a frequency, typically 50 Hz. Synchronous motors come in various sizes, from a few watts to many megawatts.
Alternators are also synchronous machines and when driven by a prime mover provide most of our electricity supply.
This chapter:
describes these machines and their operating principles.

## Slide 5: Contents
24.1 Alternators
23.2 Synchronous motors
23.3 Other types of synchronous motors

## Slide 6: 24.1 Alternators
An alternator is an AC machine that when coupled to a prime mover, generates an alternating voltage. They come in a wide range of power ratings and output voltages.
Notes: Figure 24.1

## Slide 7: Automotive alternators
Automotive alternators are typically rated at less than 1 kVA, are usually three-phase and have diodes to convert the AC output to DC in order to charge the vehicle battery.
Notes: Figure 24.2

## Slide 8: Basic alternator
An alternator has three main components: a magnetic field and a coil, in which one of them rotates relative to the other, and a set of slip rings
Notes: Figure 24.3

## Slide 9: Three-phase alternator
A three-phase alternator with an armature rotating in a magnetic field created by a DC excitation current
Notes: Figure 24.4

## Slide 10: Rotating field alternator
Two-pole rotating field three-phase alternator which produces three voltages with a phase difference of 120º
Notes: Figure 24.5 (a and b only)

## Slide 11: Salient pole rotor
Four-pole rotating field three-phase alternator and an example of a salient pole rotor
Notes: Figure 24.6

## Slide 12: Frequency and number of poles
For an alternator, the relationship between frequency, rotational speed and number of poles is found with the usual equation:
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles.

## Slide 13: Speed and number of poles
Australia and New Zealand have a power frequency of 50 Hz, requiring alternators to run at a speed that produces this frequency.
The more poles, the slower the rotational speed to produce 50 Hz.
The number of poles required for a given rotational speed and frequency is:

## Slide 14: Excitation
The field current for an alternator can be supplied by a DC shunt generator coupled to the shaft of the alternator
Notes: Figure 24.8

## Slide 15: Circuit diagram
Circuit diagram of a shunt wound exciter supplying excitation current to a three-phase alternator
Notes: Figure 24.9

## Slide 16: Circuit diagram: Brushless excitation
Circuit diagram of a brushless excitation system, in which diodes convert the output of a three-phase rotating armature alternator to provide excitation current for the main alternator
Notes: Figure 24.10

## Slide 17: Alternator output voltage
where:
= alternator phase voltage
N = number of armature turns per phase
f = frequency of the generated voltage (Hz)
 = magnetic flux per pole in webers
k = machine constant.

## Slide 18: Open-circuit characteristics
Equivalent circuit of a single-phase alternator. Under no-load conditions, VT = EG
Notes: Figure 24.11

## Slide 19
Open-circuit characteristics (2)
Open-circuit characteristic curve of an alternator, in which the field current is increased while the open-circuit voltage is measured
Notes: Figure 24.12

## Slide 20
Alternator rating
An alternator is rated by its:
terminal voltage at full load current
apparent power capability (VA rating)
frequency, which determines its rotational speed
number of phases.

## Slide 21
Alternator rating (2)
Equations to find the apparent power rating of an alternator are:
S = VI (single-phase alternator)
S = √3VLIL (three-phase alternator).

## Slide 22
Loaded characteristics
Loaded alternator characteristic curves, in which the terminal voltage is measured while the load current is increased
Notes: Figure 24.13

## Slide 23: Phasor diagrams
Phasor diagrams of an alternator for loads taking the same current, at the same terminal voltage, but at different power factors
Notes: Figure 24.14

## Slide 24: Voltage regulation
where:
= no-load voltage
= full-load voltage
The terminal voltage of an alternator is rated at its full-load value.
The regulation of an alternator is the percentage change in terminal voltage when its full rated load is removed:

## Slide 25: Voltage regulation curves
Curves showing the change in alternator terminal voltage when loads of different power factors are removed
Notes: Figure 24.15

## Slide 26: Efficiency
The efficiency of an alternator is the ratio of the true power output (Pout) and the true power input (Pin):

## Slide 27: Alternators in parallel
For a three-phase alternator to be connected in parallel with another three-phase power source:
their voltages and wave shapes should be the same, or close to
the frequencies must be identical, which means the alternator being connected must be rotating at synchronous speed
both voltages must have the same phase sequence, and be in phase with each other.

## Slide 28: Synchronising an alternator
A synchroscope indicates the difference in frequency and phase relationship between two three-phase supply systems
Notes: Figure 24.16

## Slide 29: Three lamps dark method
If all lamps glow and darken together, the phase sequence is the same. The rate at which the lamps glow and darken indicates the difference in the frequencies of the alternator and the system.
Notes: Figure 24.17

## Slide 30: Two bright, one lamp dark method
If L1 is dark and L2 and L3 are glowing, the alternator and the system are synchronised
Notes: Figure 24.18

## Slide 31: Summing up
Most alternators have a rotating field in the form of a rotor with field windings.
The windings in which the generated EMF is induced are in the form of coils wound in the stator. This winding is called the armature winding.
Alternators are designed to produce a sinusoidal voltage waveform at a rated voltage and frequency. They can be single-phase or multi-phase.

## Slide 32: Summing up (2)
The magnetic field in an alternator is produced by passing a DC excitation current through the rotor windings.
The terminal voltage of an alternator is set by the value of the excitation current.
The DC excitation source can be supplied to the rotor slip rings from a DC generator coupled to the alternator shaft.
A brushless exciter has an alternator and a three-phase rectifier built onto the shaft. This removes the need for slip rings.

## Slide 33: Summing up (3)
Alternators are rated by their full-load voltage.
The excitation current is set to achieve the correct voltage for each type of load.
When a load is removed, the terminal voltage either rises or falls, depending on the type of load.
If the load is resistive (unity power factor) or inductive (lagging power factor), the terminal voltage will rise. It will rise more for an inductive load than a resistive load.

## Slide 34: Summing up (4)
When a capacitive load is disconnected, the terminal voltage of the alternator falls.
An alternator can be connected in parallel with another alternator or power bus bars only when both are in synchronism in terms of frequency and phase difference.
When an alternator is in parallel with another power source, it will run at the synchronous speed set by the power source, either as a motor or as a generator. It will run as an alternator when its prime mover provides enough power.