- Reactive Power Optimization[RPO], Optimal Power Flow [OPF], Economic Dispatch[ED], Available Transfer Capability [ATC] Calculations

The power flow solution calculates power flows and determines bus voltages at an operating point for a given network configuration and generation and load specifications. However, it is left to the engineering judgement of the system planner to determine optimum way of system operation considering

- Operating objectives

- Operating constraints [Commercial and Security Constraints] and

- Equipment capability constraints.

Such an exercise using load flow tool is very tedious and time consuming for a practical power system with large number of operating controls and constraints.

A properly designed optimal power flow [OPF] solution provides the best and most optimum practical solution to achieve improvement in a single or multiple hierarchical objectives while respecting various constraints on the system operation. An OPF can determine the most effective subset of controls and their solution for a given operating condition to improve the specified objectives. OPF can consider different objectives for improvement such as transmission loss minimization, voltage stability improvement and minimization of system operating cost.

OPF/RPO analysis module of PowerApps is based on the Primal-dual LP programming approach and has the following features:

- Newton-Raphson load flow for solution at an operating point.

- OPF/RPO solution of multiple-islanded systems. The solution is available for each of the islands having a reference (slack) node. The reference node is automatically identified by the algorithm as the largest generator node in each island.

- Choice of objectives for the OPF/RPO (Transmission loss minimization, Voltage Stability improvement, Removal of operating violations, Economic dispatch, ATC calculations).

- Optimal load flow as per selected objectives and specified constraints

- OPF/RPO control options are active power injections, reactive power injections, shunt compensations, series compensations, phase shifters, transformer taps.

- OPF/RPO sensitivity calculations with respect to the performance objective provides information for suitable location of shunt reactive power compensation and also identifies most effective controllers for optimization.

- No limits on the number of study cases and related reports in a single execution of the program.

# PowerApps - Optimal Power Flow – Convergence Characteristics

Table of Contents

1       Introduction. 3

2       Notation. 4

3       System Data Summary and OPF convergence Characteristics. 5

3.1        6 bus Ward – Hale System.. 5

3.1.1         Loss Minimization Objective. 5

3.1.2         Loss Minimization and Economic Dispatch Objective. 5

3.2        24 Bus, Indian Test System.. 6

3.2.1         Loss Minimization Objective. 6

3.2.2         Loss Minimization and Economic Dispatch Objective. 6

3.3        89 Bus, Indian Test System.. 7

3.3.1         Loss Minimization Objective. 7

3.3.2         Loss Minimization and Economic Dispatch Objective. 7

3.4        125 Bus, Indian Test System [KPTCL] 8

3.4.1         Loss Minimization Objective. 8

3.4.2         Loss Minimization and Economic Dispatch Objective. 8

3.5        319 Bus, Indian System [KPTCL] 9

3.5.1         Loss Minimization Objective. 9

3.5.2         Loss Minimization and Economic Dispatch Objective. 9

3.6        1043 Bus, Indian Southern Grid. 10

3.6.1         Loss Minimization Objective. 10

3.6.2         Loss Minimization and Economic Dispatch Objective. 10

3.7        Gujarat Electricity Board Data [1991-94] 11

3.7.1         Loss Minimization Objective. 11

3.7.2         Loss Minimization and Economic Dispatch Objective. 11

3.8        Orissa State Electricity Board System [Around 1995] 12

3.8.1         Loss Minimization Objective. 12

3.8.2         Loss Minimization and Economic Dispatch Objective. 12

4       Conclusion. 13

# 1      Introduction

This document records the convergence characteristics the PowerApps Optimal Power Flow [OPF]. The load flow [LF] and the OPF are carried out sequentially till there is no further improvement in the performance objective or feasibility of the solution. The cycles of LF and OPF are identified as ADC in the tabular reports.

Two objective Functions are considered for illustration. The first one, only the transmission loss minimization is considered. In the second one, combined objective of economic dispatch and loss minimization are considered.

PowerApps solves the economic dispatch and transmission loss minimization as two phase optimization process as explained in the following.

1.    Obtain initial feasible load flow results

2.    Step 1 gives total generation requirement with transmission losses. Use this information for economic dispatch solution

3.    Use results of step 1 for reactive power optimization with transmission loss minimization [or any other suitable objective] to determine control settings for reactive power controls.

4.    Implement the solutions of steps 2 and 3 and go to step 1.

5.    Repeat steps 1 to 4 till no further controls can be implemented [optimum point is reached] or till specified number of load flow and optimization cycles covered.

The cost function model used by PowerApps for economic dispatch is as

All generators are assumed to have the same cost function model. All generators are assumed to be running. Consequently only the variable costs associated with MW generation is minimized.d with MW generation is minimized.

# 2      Notation

The tabular convergence characteristics report for various system has the following headings and corresponding meaning.

| Column Heading | Description of the content in tabular column |
| --- | --- |
| ADC | Load Flow Cycle Number, 0 is the base case load flow, 1 ,2 etc are after Optimizing the Controllers at the end of previous load flows 0,1 etc |
| PG Total[MW] | Total MW generation at the end of load flow |
| PL Total[MW] | Total MW Load |
| P Loss [MW] | Total MW Loss [ The objective used was minimization of transmission losses, this should be seen as improving] |
| VMAX [pu] | Maximum bus voltage at a bus in per unit as identified by load flow solution |
| VMIN [pu] | Minimum bus voltage at a bus in per unit as identified by load flow solution |
| Sv [pu] | Absolute sum of all over and all under voltage violations in per unit. Reduction in this value implies improved voltage profile. |
| Nv | Number of bus voltage violations. Reduction in this value implies improved voltage profile. |
| Qcom[MVAR] | Total MVAR compensation |
| VariableCost | Variable Cost of Generation [in any specified currency units, depending on cost model] |

# 3      System Data Summary and OPF convergence Characteristics

## 3.1     6 bus Ward – Hale System

NUMBER OF GENERATOR CONTROLS                =     2

NUMBER OF TRANSFORMER CONTROLS              =     2

NUMBER OF CAPACITOR CONTROLS                =     2

TOTAL NUMBER OF CONTROLS                    =     6

### 3.1.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 146.612327 | 135 | 11.612327 | 1.1 | 0.855219 | 0.044781 | 1 | 0 | 3693.92537 |
| 1 | 144.307479 | 135 | 9.307479 | 1.1 | 0.955202 | 0 | 0 | 10.5 | 3639.027584 |
| 2 | 144.319266 | 135 | 9.319266 | 1.1 | 0.954126 | 0 | 0 | 10.5 | 3639.304769 |

### 3.1.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total[MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 146.6123 | 135 | 11.61233 | 1.1 | 0.855219 | 0.044781 | 1 | 0 | 3693.925 |
| 1 | 143.9538 | 135 | 8.953771 | 1.1 | 0.955852 | 0 | 0 | 10.5 | 3599.887 |
| 2 | 143.7244 | 135 | 8.724368 | 1.1 | 0.955202 | 0.000013 | 1 | 10.5 | 3571.063 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further.

## 3.2     24 Bus, Indian Test System

NUMBER OF GENERATOR CONTROLS                =     4

NUMBER OF TRANSFORMER CONTROLS              =     7

NUMBER OF CAPACITOR CONTROLS                =     4

TOTAL NUMBER OF CONTROLS                    =    15

### 3.2.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 2680.472 | 2620 | 60.47208 | 1 | 0.867126 | 0.656766 | 15 | 0 | 125740.6 |
| 1 | 2671.757 | 2620 | 51.75726 | 1.05 | 0.948671 | 0.001329 | 1 | 75 | 124992.5 |
| 2 | 2671.661 | 2620 | 51.66116 | 1.05 | 0.948813 | 0.001187 | 1 | 75 | 124984.2 |

### 3.2.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 2680.472 | 2620 | 60.47208 | 1 | 0.867126 | 0.656766 | 15 | 0 | 125740.6 |
| 1 | 2668.741 | 2620 | 48.74097 | 1.05 | 0.951578 | 0 | 0 | 75 | 118690.2 |
| 2 | 2668.759 | 2620 | 48.75948 | 1.05 | 0.951667 | 0 | 0 | 75 | 118691 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further.

## 3.3     89 Bus, Indian Test System

NUMBER OF GENERATOR CONTROLS                =    12

NUMBER OF TRANSFORMER CONTROLS              =    23

NUMBER OF CAPACITOR CONTROLS                =    21

TOTAL NUMBER OF CONTROLS                    =    56

### 3.3.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 2203.259 | 2049.87 | 153.3887 | 1.010935 | 0.749948 | 5.525923 | 51 | 0 | 54213.98 |
| 1 | 2169.692 | 2049.87 | 119.8221 | 1.05 | 0.923664 | 0.065156 | 6 | 266.904 | 53379.55 |
| 2 | 2164.465 | 2049.87 | 114.5953 | 1.05 | 0.951416 | 0 | 0 | 375.1516 | 53253.67 |

### 3.3.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 2203.259 | 2049.87 | 153.3887 | 1.010935 | 0.749948 | 5.525923 | 51 | 0 | 54213.98 |
| 1 | 2165.328 | 2049.87 | 115.4578 | 1.05 | 0.926642 | 0.049282 | 4 | 266.904 | 52731.02 |
| 2 | 2158.131 | 2049.87 | 108.2615 | 1.051578 | 0.954055 | 0.002966 | 4 | 364.3801 | 52280.68 |
| 3 | 2157.065 | 2049.87 | 107.1954 | 1.054449 | 0.94652 | 0.012911 | 8 | 364.3801 | 52210.73 |
| 4 | 2155.865 | 2049.87 | 105.9951 | 1.071999 | 0.952598 | 0.03088 | 8 | 320.4141 | 52175.45 |
| 5 | 2154.255 | 2049.87 | 104.3852 | 1.074034 | 0.946683 | 0.03885 | 7 | 302.552 | 52124.63 |
| 6 | 2153.81 | 2049.87 | 103.9396 | 1.074893 | 0.958409 | 0.048713 | 12 | 317.6971 | 52107.12 |
| 7 | 2153.727 | 2049.87 | 103.8568 | 1.056282 | 0.958623 | 0.021778 | 9 | 317.6971 | 52099.53 |
| 8 | 2153.652 | 2049.87 | 103.7817 | 1.057435 | 0.959246 | 0.020234 | 9 | 317.6971 | 52097.58 |
| 9 | 2153.562 | 2049.87 | 103.6917 | 1.074952 | 0.95944 | 0.045557 | 10 | 317.6971 | 52095.26 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further

3.    The algorithm went on for full specified 10 number of load flow and optimization cycles with marginal improvements in the latter cycles..

## 3.4     125 Bus, Indian Test System [KPTCL]

NUMBER OF GENERATOR CONTROLS                =    26

NUMBER OF TRANSFORMER CONTROLS              =    25

NUMBER OF CAPACITOR CONTROLS                =    18

TOTAL NUMBER OF CONTROLS                    =    69

### 3.4.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4833.519 | 4643.89 | 189.6287 | 1.03 | 0.740645 | 3.027959 | 61 | 0 | 139108.1 |
| 1 | 4795.075 | 4643.89 | 151.1846 | 1.05 | 0.927916 | 0.127677 | 10 | 275 | 137096.3 |
| 2 | 4789.937 | 4643.89 | 146.0468 | 1.058903 | 0.94073 | 0.034106 | 7 | 290.5083 | 136831.9 |
| 3 | 4789.367 | 4643.89 | 145.4768 | 1.058903 | 0.941461 | 0.031383 | 10 | 295.5083 | 136802.6 |
| 4 | 4789.521 | 4643.89 | 145.6313 | 1.058903 | 0.941266 | 0.032697 | 9 | 295.5083 | 136810.2 |

### 3.4.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4833.519 | 4643.89 | 189.6287 | 1.03 | 0.740645 | 3.027959 | 61 | 0 | 139108.1 |
| 1 | 4788.748 | 4643.89 | 144.8576 | 1.05 | 0.929997 | 0.102979 | 9 | 275 | 131047.6 |
| 2 | 4785.032 | 4643.89 | 141.1423 | 1.068482 | 0.942649 | 0.063537 | 12 | 280 | 130853.6 |
| 3 | 4784.729 | 4643.89 | 140.8385 | 1.068482 | 0.945397 | 0.065103 | 13 | 280 | 130857.6 |
| 4 | 4784.716 | 4643.89 | 140.8263 | 1.068482 | 0.945329 | 0.063751 | 13 | 280 | 130839.3 |
| 5 | 4784.338 | 4643.89 | 140.4477 | 1.068482 | 0.945977 | 0.060669 | 14 | 280 | 130822.6 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further

## 3.5     319 Bus, Indian System [KPTCL]

NUMBER OF GENERATOR CONTROLS                =    22

NUMBER OF TRANSFORMER CONTROLS              =    77

NUMBER OF CAPACITOR CONTROLS                =    47

TOTAL NUMBER OF CONTROLS                    =   146

### 3.5.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4563.446 | 4275 | 288.446 | 1 | 0.637032 | 21.68275 | 245 | 0 | 172591.8 |
| 1 | 4496.877 | 4275 | 221.8772 | 1.05 | 0.933239 | 0.039275 | 5 | 296.9124 | 166570.9 |
| 2 | 4492.448 | 4275 | 217.4478 | 1.05 | 0.950973 | 0 | 0 | 370.7209 | 166176.5 |
| 3 | 4492.045 | 4275 | 217.0445 | 1.05 | 0.952069 | 0 | 0 | 394.4941 | 166140.7 |

### 3.5.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4563.446 | 4275 | 288.446 | 1 | 0.637032 | 21.68275 | 245 | 0 | 172591.8 |
| 1 | 4483.542 | 4275 | 208.542 | 1.05 | 0.93653 | 0.023548 | 3 | 296.9124 | 151933.7 |
| 2 | 4480.509 | 4275 | 205.5087 | 1.052389 | 0.951147 | 0.002389 | 1 | 355.0025 | 151692.3 |
| 3 | 4480.031 | 4275 | 205.0313 | 1.052895 | 0.952047 | 0.002895 | 1 | 380.7686 | 151657.1 |
| 4 | 4480.096 | 4275 | 205.0962 | 1.052876 | 0.949652 | 0.003224 | 2 | 380.7686 | 151689.3 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further

## 3.6     1043 Bus, Indian Southern Grid

NUMBER OF GENERATOR CONTROLS                =    66

NUMBER OF TRANSFORMER CONTROLS              =   138

NUMBER OF CAPACITOR CONTROLS                =   590

TOTAL NUMBER OF CONTROLS                    =   794

### 3.6.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 13222.2 | 12545.15 | 677.0469 | 1.021436 | 0.553079 | 79.19027 | 829 | 0 | 415815.1 |
| 1 | 13222.29 | 12545.15 | 677.1386 | 1.05 | 0.701053 | 11.32251 | 267 | 5237.901 | 433129.7 |
| 2 | 13173.37 | 12545.15 | 628.2183 | 1.05435 | 0.759467 | 2.142998 | 85 | 5706.414 | 431965.5 |
| 3 | 13168.13 | 12545.15 | 622.9804 | 1.088152 | 0.766347 | 1.755495 | 68 | 5776.631 | 431846.7 |
| 4 | 13167.27 | 12545.15 | 622.1214 | 1.086513 | 0.76956 | 1.715472 | 68 | 5776.631 | 431827.3 |
| 5 | 13167.53 | 12545.15 | 622.3756 | 1.086294 | 0.769564 | 1.695118 | 64 | 5776.631 | 431833.1 |

Notes:

1.    The initial load flow corresponds to infeasible [not converged] load flow and hence its variable cost is not valid. Load flow solution at the point of minimum mismatch was used for optimization solution.

2.    Losses and Variable Cost however, steadily improve from converged load flow solution of ADC 1 and above.

### 3.6.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 13222.2 | 12545.15 | 677.0469 | 1.021436 | 0.553079 | 79.19027 | 829 | 0 | 415815.1 |
| 1 | 13234.75 | 12545.15 | 689.5994 | 1.050258 | 0.702001 | 11.97724 | 276 | 5237.901 | 416831.6 |
| 2 | 13186.04 | 12545.15 | 640.8946 | 1.050674 | 0.758889 | 2.236873 | 86 | 5671.229 | 416152.7 |
| 3 | 13179.77 | 12545.15 | 634.6243 | 1.051316 | 0.7699 | 1.72662 | 63 | 5642.4 | 414490.6 |
| 4 | 13178.79 | 12545.15 | 633.6431 | 1.053028 | 0.772968 | 1.707763 | 62 | 5642.4 | 414252.3 |
| 5 | 13178.72 | 12545.15 | 633.5735 | 1.052937 | 0.772805 | 1.709201 | 62 | 5642.4 | 414220.1 |
| 6 | 13178.68 | 12545.15 | 633.5295 | 1.052962 | 0.77285 | 1.707772 | 63 | 5643.69 | 414219.2 |
| 7 | 13178.73 | 12545.15 | 633.584 | 1.052942 | 0.772815 | 1.707775 | 61 | 5642.09 | 414220.5 |
| 8 | 13178.7 | 12545.15 | 633.5527 | 1.052969 | 0.772863 | 1.705596 | 63 | 5643.803 | 414219.7 |

Notes:

1.    The initial load flow corresponds to infeasible [not converged] load flow and hence its variable cost is not valid. Load flow solution at the point of minimum mismatch was used for optimization solution.

2.    Losses and Variable Cost however, steadily improve from converged load flow solution of ADC 1 and above.

3.    Variable Costs Improve better with this objective compared to plain loss minimization objective.

4.    Over voltages are controlled better with this combined objective compared to plain loss minimization objective.

## 3.7     Gujarat Electricity Board Data [1991-94]

NUMBER OF GENERATOR CONTROLS                =    20

NUMBER OF TRANSFORMER CONTROLS              =    23

NUMBER OF CAPACITOR CONTROLS                =    11

TOTAL NUMBER OF CONTROLS                    =    54

### 3.7.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4047.642 | 3933 | 114.6419 | 1.05 | 0.713986 | 3.145116 | 54 | 0 | 107107 |
| 1 | 4023.298 | 3933 | 90.29814 | 1.05 | 0.944865 | 0.00914 | 2 | 260 | 106210.6 |
| 2 | 4023.792 | 3933 | 90.7917 | 1.05 | 0.971693 | 0 | 0 | 280 | 106228.5 |
| 3 | 4023.614 | 3933 | 90.61445 | 1.05 | 0.969762 | 0 | 0 | 280 | 106222.1 |
| 4 | 4023.245 | 3933 | 90.24471 | 1.050238 | 0.973029 | 0.000238 | 1 | 280 | 106208.5 |

### 3.7.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 4047.642 | 3933 | 114.6419 | 1.05 | 0.713986 | 3.145116 | 54 | 0 | 107107 |
| 1 | 4018.345 | 3933 | 85.3453 | 1.05 | 0.947386 | 0.004102 | 2 | 260 | 104144.6 |
| 2 | 4019.783 | 3933 | 86.78281 | 1.05 | 0.973307 | 0 | 0 | 280 | 104185.7 |
| 3 | 4019.389 | 3933 | 86.38881 | 1.05 | 0.972943 | 0 | 0 | 280 | 104165.9 |
| 4 | 4019.641 | 3933 | 86.64112 | 1.05 | 0.970029 | 0 | 0 | 280 | 104180.1 |
| 5 | 4019.269 | 3933 | 86.26866 | 1.05 | 0.97416 | 0 | 0 | 280 | 104163.7 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have reduced further

## 3.8     Orissa State Electricity Board System [Around 1995]

NUMBER OF GENERATOR CONTROLS                =    14

NUMBER OF TRANSFORMER CONTROLS              =    19

NUMBER OF CAPACITOR CONTROLS                =    13

TOTAL NUMBER OF CONTROLS                    =    46

### 3.8.1      Loss Minimization Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 3955.887 | 3770 | 185.8874 | 1.04 | 0.654134 | 8.09204 | 82 | 0 | 119355.2 |
| 1 | 3922.079 | 3770 | 152.0789 | 1.05 | 0.908798 | 0.298497 | 25 | 185.1513 | 117368.7 |
| 2 | 3916.141 | 3770 | 146.141 | 1.05 | 0.925086 | 0.061712 | 8 | 185.1513 | 117024.5 |
| 3 | 3915.149 | 3770 | 145.1491 | 1.05 | 0.928355 | 0.038809 | 7 | 193 | 116967.1 |

### 3.8.2      Loss Minimization and Economic Dispatch Objective

| ADC | PG Total [MW] | PL Total [MW] | P Loss [MW] | VMAX [pu] | VMIN [pu] | Sv [pu] | Nv | Qcom [MVAR] | Variable Cost |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 3955.887 | 3770 | 185.8874 | 1.04 | 0.654134 | 8.09204 | 82 | 0 | 119355.2 |
| 1 | 3933.614 | 3770 | 163.6135 | 1.05 | 0.903117 | 0.415851 | 31 | 185.1513 | 112740.3 |
| 2 | 3928.594 | 3770 | 158.5938 | 1.05 | 0.921461 | 0.134894 | 14 | 193 | 112511 |
| 3 | 3925.758 | 3770 | 155.758 | 1.05 | 0.927761 | 0.026561 | 4 | 211.2418 | 112379.5 |

Notes:

1.    Variable costs are minimized with economic dispatch

2.    With economic dispatch losses also have NOT reduced further

# 4      Conclusion

The results for 8 systems starting from 6 bus test system to 1043 bus practical Indian Grid system, indicates the robustness and dependability of the PowerApps OPF algorithm

In most cases as observed by this author , the combined objective of economic dispatch and loss minimization was more effective, as compared to only transmission loss minimization objective