## Slide 1
Power System Security in the New Industry Environment: Challenges and Solutions
Prabha Kundur
Powertech Labs Inc.
Surrey, B.C. Canada
Prabha Kundur
Powertech Labs Inc.
Surrey, B.C. Canada
IEEE Toronto Centennial Forum on Reliable Power Grids in Canada
October 3, 2003

## Slide 2: Power System Security
Security of a power system is affected by three factors:
Characteristics of the physical system:
  the integrated generation, transmission and distribution system
  protection and control systems
Business structures of owning and operating entities
The regulatory framework

## Slide 3: Challenges to Secure Operation of Today's Power Systems
Power Systems are large complex systems covering vast areas
  national/continental grids
  highly nonlinear, high order system
Many processes whose operations need to be coordinated
  millions of devices requiring harmonious interplay

## Slide 4: Challenges to Secure Operation of Today's Power Systems (cont'd)
Complex modes of instability
  global problems
  different forms of instability: rotor angle, voltage, frequency
"Deregulated" market environment
  many entities with diverse business interests
  system expansion and operation driven largely by economic drivers; lack of coordinated planning

## Slide 5: Traditional Approach to Power System Stability
The November ,9 1965 blackout of Northeast US and Canada had a profound effect on consideration of stability in system design and operation
  focus, however, has been largely limited to transient (angle) stability
The changing characteristics of power systems requires careful consideration of other aspects of stability
  Interarea oscillations; voltage stability
System designed/operated to withstand loss of a single element
Operating limits based on off-line studies
  scenarios based on judgment and experience

## Slide 6: November 9, 1965 Blackout of Northeast US and Ontario

## Slide 7: November 9, 1965 - Blackout of Northeast US and Ontario
Clear day with mild weather
Load levels in the regional normal
Problem began at 5:16 p.m.
Within a few minutes, there was a complete shut down of electric service to
  virtually all of the states of New York, Connecticut, Rhode Island, Massachusetts, Vermont
  parts of New Hampshire, New Jersey and Pennsylvania
  most of Ontario
Nearly 30 million people were without power for about 13 hours

## Slide 8: Events that Caused the 1965 Blackout
The initial event was the operation of a backup relay at Beck GS in Ontario near Niagara Falls
  opened circuit Q29BD, one of five 230 kV circuits connecting Beck GS to load centers in Toronto and Hamilton
Prior to opening of Q29BD, the five circuits were carrying
  1200 MW of Beck generation, and
  500 MW import from Western NY State on Niagara ties
Net import from NY 300 MW
Loading on Q29BD was 361 MW at 248 kV;
The relay setting corresponded to 375 MW

## Slide 9: Events that Caused the 1965 Blackout (cont’d)
Opening of Q29BD resulted in sequential tripping of the remaining four parallel circuits
Power flow reversed to New York
  total change of 1700 MW
Power surge back to Ontario via St. Lawrence ties
  ties tripped by protective relaying
Generators in Western New York and Beck GS lost synchronism, followed by cascading outages
After about 7 seconds from the initial disturbance
  system split into several separate islands
  eventually most generation and load lost; inability of islanded systems to stabilize

## Slide 10: Formation of Reliability Councils
Northeast Power Coordinating Council (NPCC) formed in January 1966
  to improve coordination in planning and operation among utilities in the region that was blacked out
  first Regional Reliability Council (RRC) in North America
Other eight RRCs formed in the following months
National/North American Electric Reliability Council (NERC) established in 1968
Detailed reliability criteria were developed
Procedures for exchange of data and conducting stability studies were established
  many of these developments has had an influence on utility practices worldwide
  still largely used

## Slide 11: Examples of Recent Major System Disturbances/Blackouts
July 2, 1996 disturbance of WSCC (Western North American Interconnected) System
August 10, 1996 disturbance of WSCC system
1998 power failure of Auckland business districts, New Zealand
March 11, 1999 Brazil blackout
July 29, 1999 Taiwan disturbance
August 14, 2003 blackout of Northeast U.S. and Ontario

## Slide 12: July 2, 1996 WSCC (WECC) Disturbance

## Slide 13: WSCC July 2, 1996 Disturbance
Started in Wyoming and Idaho area at 14:24:37
Loads were high in Southern Idaho and Utah; High temperature around 38°C
Heavy power transfers from Pacific NW to California
  Pacific AC interties - 4300 MW (4800 rating)
  Pacific HVDC intertie - 2800 MW (3100 capacity)

## Slide 14: WSCC July 2, 1996 Disturbance (cont'd)

## Slide 15: WSCC July 2, 1996 Disturbance (cont'd)
LG fault on 345 kV line from Jim Bridger 2000 MW plant in Wyoming to Idaho due to flashover to a tree
  tripping of parallel line due to relay misoperation
Tripping of two (of four) Jim Bridger units as stability control; this should have stabilized the system
Faulty relay tripped 230 kV line in Eastern Oregon
Voltage decay in southern Idaho and slow decay in central Oregon

## Slide 16: WSCC July 2, 1996 Disturbance (cont’d)
About 24 seconds later, a long 230 kV line (Amps line) from western Montana to Southern Idaho tripped
  zone 3 relay operation
  parallel 161 kV line subsequently tripped
Rapid voltage decay in Idaho and Oregon
Three seconds later, four 230 kV lines from Hells Canyon to Boise tripped
Two seconds later, Pacific intertie lines separated
Cascading to five islands 35 seconds after initial fault
2.2 million customers experienced outages; total load lost 11,900 MW
Voltage Instability!!!

## Slide 17: WSCC July 2, 1996 Disturbance (cont'd)

## Slide 18: WSCC July 2, 1996 Disturbance (cont'd)

## Slide 19: ETMSP was Used to Replicate Disturbance in Time Domain
MEASURED RESPONSE
SIMULATED RESPONSE

## Slide 20: August 10, 1996 WSCC (WECC) Disturbance

## Slide 21: WSCC August 10, 1996 Disturbance
High ambient temperatures in Northwest; high power transfer from Canada to California
Prior to main outage, three 500 kV line sections from lower Columbia River to load centres in Oregon were out of service due to tree faults
California-Oregon Interties loaded to 4330 MW north to south
Pacific DC Intertie loaded at 2680 MW north to south
2300 MW flow from British Columbia
Growing 0.23 Hz oscillations caused tripping of lines resulting in formation of four islands
  loss of 30,500 MW load

## Slide 22: August 10th, 1996 WSCC Event

## Slide 23: WSCC August 10, 1996 Disturbance (cont'd)
Malin - Round Mountain MW Flow
2300
2400
2500
2600
2700
2800
2900
3000
0
3
6
9
12
16
19
22
25
28
31
34
37
40
43
47
50
53
56
59
62
65
68
71
74
Time in Seconds

## Slide 24: WSCC August 10, 1996 Disturbance (cont'd)
As a result of the undamped oscillations, the system split into four large islands
Over 7.5 million customers experienced outages ranging from a few minutes to nine hours! Total load loss 30,500 MW

## Slide 25: ETMSP was Used to Replicate Disturbance in Time Domain
MEASURED RESPONSE
SIMULATED RESPONSE

## Slide 26: Sites Selected for PSS Modifications
San Onofre (Addition)
Palo Verde (Tune existing)

## Slide 27: Power System Stabilizers
With existing controls
Eigenvalue = 0.0597 + j 1.771
Frequency = 0.2818 Hz
Damping = -0.0337
With PSS modifications
Eigenvalue = -0.0717 + j 1.673
Frequency = 0.2664
Damping = -0.0429

## Slide 28: March 11, 1999 Brazil Blackout

## Slide 29: March 11, 1999 Brazil Blackout
Time: 22:16:00h, System Load: 34,200 MW
Description of the event:
  L-G fault at Bauru Substation as a result of lightning causing a bus insulator flashover
  the bus arrangement at Bauru such that the fault is cleared by opening five 440 kV lines
  the power system survived the initial event, but resulted in instability when a short heavily loaded 440 kV line was tripped by zone 3 relay
  cascading outages of several power plants in Sao Paulo area, followed by loss of HVDC and 750 kV AC links from Itaipu
  complete system break up: 24,700 MW load loss; several islands remained in operation with a total load of about 10,000 MW

## Slide 30: March 11, 1999 Brazil Blackout (cont'd)
Measures to improve system security:
  Joint Working Group comprising ELECTROBRAS, CEPEL and ONS staff formed
    organized activities into 8 Task Forces
  Four international experts as advisors
Remedial Actions:
  power system divided into 5 security zones: regions with major generation and transmission system; emergency controls added for enhancing stability
  improved layout and protection of major EHV substations
  improved maintenance of substation equipment and protection/control equipment
  improved restoration plans

## Slide 31
What Can We Do To Prevent Blackouts?

## Slide 32: Methods of Enhancing Security
Impractical to achieve complete immunity to blackouts
  need to strike a balance between economy and security
Good design and operating practices could significantly minimize the occurrence and impact of widespread outages
  Reliability criteria
  On-line security assessment
  Robust stability controls
  Coordinated emergency controls
  Real-time system system monitoring and control
  Wide-spread use of distributed generation

## Slide 33: Reliability Criteria
At present, systems designed and operated to withstand
  loss of any single element preceded by single-, double-, or three-phase fault
  referred to as "N-1 criterion"
Need for using risk-based security assessment
  consider multiple outages
  account for probability and consequences of instability
Built-in overall strength or robustness best defense against catastrophic failures!

## Slide 34: Enhancement of Stability: Controls
Greater use of on stability controls
  excitation control (PSS), FACTS, HVDC, secondary voltage control
  multi-purpose controls
Coordination, integration and robustness present challenges
  good control design procedures and tools have evolved
Hardware design should provide
  high degree of functional reliability
  flexibility for maintenance and testing
Industry should make better use of controls!

## Slide 35: Development of a Good "Defense Plan" against Extreme Contingencies
Judicious choice of emergency controls
  protection against multiple outages
  identification of scenarios based on past experience, knowledge of unique characteristics of system, probabilistic approach
Coordination of different emergency control schemes
  complement each other
  act properly in complex situations
Response-based emergency controls should generally be preferred
  "self-healing" power systems
Need for advancing this technology!

## Slide 36: State-of-the-Art On-Line Dynamic Security Assessment (DSA)
Practical tools with the required accuracy, speed and robustness
  a variety of analytical techniques integrated
  distributed hardware architecture using low cost PCs
  integrated with energy management system
Capable of assessing rotor angle stability and voltage stability
  determine critical contingencies automatically
  security limits/margins for all desired energy transactions
  identify remedial measures
The industry has yet to take full advantage of these developments!

## Slide 37: Management of System Reliability
Roles and responsibilities of individual entities
  well chosen, clearly defined and properly enforced
Coordination of reliability management
Need for a single entity with overall responsibility for security of entire interconnected system
  real-time decisions
System operators with high level of expertise in system stability
  phenomena, tools

## Slide 38: Future Trends in DSA: Intelligent Systems
Knowledge base created using simulation of a large number cases and system measurements
Automatic learning, data mining, and decision trees to build intelligent systems
Fast analysis using a broad knowledge base and automatic decision making
Provides new insight into factors and system parameters affecting stability
More effective in dealing with uncertainties and large dimensioned problems
We just completed a PRECARN project

## Slide 39: DSA Using Intelligent Systems

## Slide 40: Real-Time Monitoring and Control: An Emerging Technology
Advances in communications technology have made it possible to
  monitor power systems over a wide area
  remotely control many functions
Research on use of multisensor data fusion technology
  process data from different monitors, integrate and process information
  identify phenomenon associated with impending emergency
  make intelligent control decisions
A fast and effective way to predict onset of emergency conditions and take remedial actions

## Slide 41: Distributed Generation (DG)
Offer significant economic, environmental and security benefits
DG becoming increasingly cost competitive
Microturbines
  small, high speed power plants
  operate on natural gas, future units may use diesel or gas from landfills

## Slide 42: Distributed Generation (DG) (cont'd)
Fuel Cells
  combine hydrogen with oxygen from air to generate electricity
  hydrogen may be supplied from an external source or generated inside fuel by reforming a hydrocarbon fuel
  high efficiency, non-combustion, non-mechanical process
Particularly attractive in Ontario
  generate hydrogen during light load using nuclear generation
Not vulnerable to power grid failure due to system instability or natural calamities!

## Slide 43: Summary
The new electricity supply industry presents increasing challenges for stable and secure operation of power systems
State-of-the-art methods and tools have advanced our capabilities significantly facing the challenges
  comprehensive stability analysis tools
  coordinated design of robust stability controls
  on-line dynamic security assessment
Industry yet to take full advantage of these developments!
Need to review and improve
  the reliability criteria
  the process for managing "global" system reliability

## Slide 44: Summary (cont'd)
Emerging technologies which can better deal with growing uncertainties and increasing complexities of the problem
  Intelligent Systems for DSA
  Real-time monitoring and control
  "Self-healing" power systems
Wide-spread use of distributed generation is a cost effective, environmentally friendly means of minimizing the impact of power grid failures

## Slide 45: Vulnerability of B.C. Power System to Blackouts
Transmission is not very meshed
  power transmitted from large sources of hydroelectric generation over 500 kV lines
Most of the power generation is from hydroelectric plants
  simple and rugged
  can be restored quickly
Good set of emergency controls
  generation and load tripping
  braking resistor
Disturbances in western interconnected system result in separation into islands
Less vulnerable to complete blackout !

## Slide 46: Terminology

## Slide 47: Power System Security
Security: the degree of risk in the ability to survive imminent disturbances (contingencies) without interruption of customer service
  depends on the operating condition and the contingent probability of a disturbance
To be secure, the power system must:
  be stable following a contingency, and
  settle to operating conditions such that no physical constraints are violated
The power system must also be secure against contingencies that would not be classified as stability problems, e.g. damage to equipment such as failure of a cable

## Slide 48: Power System Security (cont'd)
Stability: the continuance of intact operation of the power system following a disturbance
Reliability: the probability of satisfactory operation over the long run
  denotes the ability to supply adequate electric service on a nearly continuous basis, with few interruptions over an extended period
Stability and security are time-varying attributes; Reliability is a function of time-average performance