CHECKLIST 012

Electrical installations

Electrical installations: construction and demolition sites

b

| Inspected by: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Inspection date: |  |  |  |  |  |  |
| Clause | AS/NZS 3012 Requirements |  |  |  |  |  |
| 1.2 | All wiring installed according to AS3000 Wiring rules in addition to AS3012 requirements. |  | Yes |  | No |  |
| 2.1.2 | All electrical equipment and lighting supplied from a 30mA RCD protected circuit breaker(s). |  | Yes |  | No |  |
| 2.1.3 | Source of supply identified. |  | Yes |  | No |  |
| 2.3.1.1 | Switchboard readily accessible. |  | Yes |  | No |  |
| 2.3.2.1(ab) | Switchboard of robust construction with a minimum IP23 rating. |  | Yes |  | No |  |
| 2.3.2.1 (c) | Live parts effectively protected and warning sign attached along an electric shock symbol. |  | Yes |  | No |  |
| 2.3.2.1 (d) | Insulated tie bar for extension leads to prevent strain on socket /outlet |  | Yes |  | No |  |
| 2.3.2.1 (e) | Switchboard door is lockable, non-removable without a tool and fitted with a retention device to stay in open position. |  |  |  |  |  |
| 2.3.2.1 (e) | Switchboard has means of safe entry of leads and label: KEEP CLOSED –RUN LEADS THROUGH BOTTOM |  | Yes |  | No |  |
| 2.3.3 | Switchboard mounted on a polo, structure, wall or suitably designed free standing design. |  | Yes |  | No |  |
| 2.4.1 | Switchboard gas a main isolation switch capable of isolation all downstream circuits. |  | Yes |  | No |  |
| 2.4.2 | Main switch capable of being locked or within a lockable space. |  | Yes |  | No |  |
| 2.4.3 | Main switch labelled appropriately: MAIN SWITCH or DISTRIBUTION BOARD ISOLATION SWITCH or similar. |  | Yes |  | No |  |
| 2.5.3 | Construction wiring installed in appropriate conduit to protect against mechanical damage. |  | Yes |  | No |  |
| 2.5.4 | Construction wiring labelled with yellow tape with words ‘construction wiring’ at distances not longer than 5m. |  | Yes |  | No |  |
| 2.6.9 | Extension leads supported by stands or insulated hooks. |  | Yes |  | No |  |
| 2.7.1 | Adequate lighting provided for safe work. |  | Yes |  | No |  |
| 2.7.2 | Lighting is mechanically protected. |  | Yes |  | No |  |

www.act.gov.au/accesscbr

Electrical installations

| 2.7.3 | Emergency lighting adequate for safe exit of workers (if applicable). |  | Yes |  | No |
| --- | --- | --- | --- | --- | --- |
| 2.8.1 | If a lift shaft is present, the final sub-circuit feeding it is locked and tagged to prevent inadvertent isolation of supply. |  | Yes |  | No |
| 2.9 | Socket outlets in site sheds and other transportable structures are RCD protected. |  | Yes |  | No |
| 3.8.3 | Portable equipment including power leads are inspected at three-monthly intervals. |  | Yes |  | No |
| 3.8.3 | Portable RCD’s trip time is tested every 3 months. |  | Yes |  | No |
| 3.8.3 | Switchboards, wiring and site sheds are inspected at six-monthly intervals. |  | Yes |  | No |
| 3.10 | Register available for equipment and includes records of testing and tagging. RCD trip time results and list of repaired equipment. |  | Yes |  | No |

Action required:

Re-inspected by:

Compliance date:

www.act.gov.au/accesscbr