UEPOPS349B - Operate Local H.V. switchgear ASSESSMENT

Q1.Describe the risks and dangers in power station and outline the recommended safety

Q2.equipments and emergency procedures.

Q3.Outline the process of maintenance work in substation.

  - OHS risk control measures and procedures in preparation for the work are followed

Ref-Advanced Diploma in Electrical Engineering Exercises Page 3 -Q17+18  Page 4 Q21+22

Q4. Write down the check list to perform the tasks in substation.

Q5. Write down the safety procedures and methods to assess the risk and to reduce the

risk.

Q6..Write down the code of practice for working near exposed main and apparatus.

Q7.Which precautions are to be emphasized when working in substation?

1.3  The likely extent of work to be undertaken is envisaged from reports and/or discussions with

appropriate person(s)

Q8. Write down the risk reduction procedures in maintenance work to discuss with work manager. (Ref-Advanced Diploma in Electrical Engineering Exercises Page 2 Q12)

  - Advice is sought from the work supervisor to ensure the work is coordinated effectively withothers.

Answer the following questions to seek the advice from work supervisor in the following aspects.

Q9. What are the risks?

Q10.How are the risks classified?

Q12.How can the risk be evaluated?

Q12.How will you manage the risk? Ref-Advanced Diploma in Electrical Engineering Exercises Page 2 Q8 to 11)

  - Sources of materials that may be required for the work are established in accordance with established procedures.

Submit the following assignment questions

Ref-Advanced Diploma in Electrical Engineering Exercises Page 123)

The practice questions are organized to find out the protection system equipments and materials together with relevant theory

15) Over current and earth fault protection

Slide 1+2

Q1.Sketch three phase over current protection.

Q2.Sketch three phase earth fault relay protection.

Slide 3+4+5

Q3.Explain the operation of directional element with sketch.

Slide 6

Q4.Locate the position of reverse power relay in power line.

Slide 7

Q5.Sketch the connection of combined protection scheme that contains two over current relays &

one earth fault relay to provide phase to phase and earth protection.

Q6.How does directional element of relay perform?

Slide 8

Q7.Locate directional and non directional element in a ring circuit.

1.6  Tools, equipment and testing devices needed to take measurements are obtained in accordance with established procedures and checked for

correct operation and safety.

Ref-Advanced Diploma in Electrical Engineering Exercises Page 128)

.Testing of protection current & potential transformer and relevant questions are arranged to provide this competency component.

Slide 5

Q52.Explain (a) AC ratio check (b) DC polarity check (c)Three phase polarity test for three phase CT

Slide 6

Q53.How will you interpose & sum CT & PT?

- Solve problems in energy supply network protection  equipment and system.

  - OHS risk control measures and procedures for carrying out the work are followed.

As per 1.1 to 1.3

  - The need to test or measure live is determined in strict accordance with OHS requirements and when necessary conducted within established safety procedures.

Ref-Advanced Diploma in Electrical Engineering Exercises Page 126)

Live testing of protective relay system and depermination of characteristics  and relevant questions are arrrranged to provide this competency component.

(25) Distance protection scheme

Slide 1

Q30.Explain the distance protection scheme with sketch.

Slide 2

Q31.Explain the operation and construction of distance relay with sketch.

Slide 3

Q32.Explain the characteristics of distance relay.

Slide 4

Q33.Describe the directional distance relay with sketch.

Slide 5

Q34.What is the relation between maximum reach & relay characteristics.

Slide 6+7

Q35.Explain the zones for distance protection scheme.

Slide 8

Q36.Explain the operation of three phase distance relay.

Slide 9

Q37.Explain maximum reach and maximum reach angle.

  - Circuits/machines/plant are checked as being isolated where necessary in strict accordance OHS requirements and procedures

As per 1.3

  - Safety hazards resulting from the reports and risk control measures devised and implemented in consultation with appropriate personnel.

As per 1.3

2.5 Problem solving is approached methodically drawing on knowledge of energy supply network protection equipment and systems

using measured and calculated values of circuit/apparatus parameters.

2.12  Problem solving activities are carried out without damage to apparatus, circuits, the surrounding environment or services and using sustainable

energy practices.

| EKAS COMPONENT | Question No | Questions |
| --- | --- | --- |
| KS01-TIS68A Electrical power system protection Evidence shall show an understanding of protection methods and devices for electrical power systems to an extent indicated by the following aspects: T1 Protection fundamentals encompassing:  purpose of protection  features of a protection scheme T2 Instrument transformers for protection encompassing:  Operating principles  Applications of current transformers  Applications of voltage transformers T3 Feeder protection encompassing:  fuse protection  overcurrent & earth fault  sensitive earth fault  unit schemes  distance protection  trip/close sequences for feeders  recloser/sectionaliser systems T4 Transformer protection encompassing:  overheating protection  overcurrent protection  restricted earth fault protection  differential protection  oil and gas devices T5 Busbar protection encompassing:  types of fault  requirements of busbar protection  system protection  frame-earth protection T6 Surge protection encompassing:  voltage surges  surge diverters  arcing horns | 1 2 3 4 5 6 7 Total 70 marks 8 9 10 Total 100 marks | What is power system protection scheme? (5 marks) What equipments are included in power system protection scheme? (5 marks) Explain the functions of the following devices included in a power system protection Scheme. CT, PT, Fault Detector, Tripping Circuit (10 marks) Sketch the construction of - Balanced Beam Relay Connection Diagram of Relay Tripping Circuit (10 marks) Sketch the connection diagram of combination protection scheme that contains two Over current relays and one earth fault relay to provide phase to phase and phase to earth protection.. (10 marks) Locate relay protection scheme for given system when fault occurs at point F. (20 marks) Sketch curve for discrimination by both time and current of the following power system.. (20 marks) How will you adjust Definite Minimum Time point on relay curve? ( 5 marks) What is “Pick Up” of relay? ( 5 marks Sketch the vector diagram for primary, secondary main windings of Star Delta Power Transformer . ( 10 marks) |

2.6 Circuit/apparatus components are dismantled where necessary and parts stored to protect them against loss or damage

Ref-Advanced Diploma in Electrical Engineering Exercises Page 128)

To convert the analog relaying system to digital relay system, the dismantling of origin components and assembly of new system components are to be done. The following questions and activities provide this competency component.

(29) Digital relay+ Telecommunication for protection

Slide 1

Q54.What is digital relay?

Slide 2+4

Q55.Sketch the flow diagram of digital relay operation.

Slide 3+4

Q56.Sketch DAC system

Slide 5

Q57.Explain busbar protection with sketch

Slide 6

Q58.Write line & busbar protection with sketch.

Slide 7

Q59.Sketch the operation of digital relay.

2.7  Circuits/components are rechecked and their operational status is confirmed.

Ref-Advanced Diploma in Electrical Engineering Exercises Page 129)

To determine the operational status of protection system, it needs to ensure relay operation sequence, the sequential relay protection system and characteristics are to be investigated. The following activities and questions provide this competency.

(32)Over current & earth fault protection , Directional protection, operating characteristics

Slide 1

Q64.Sketch the diagram of over current protection

Slide 2

Q65.Sketch earth fault relay protection diagram.

Slide 3

Q66.Sketch the combined over current and earth fault protection and explain it’s operation.

Slide 4

Q67.Explain the operation of directional relay with diagram.

Slide 5+6+7+8

Q68.Locate directional & non directional elements in ring system.

Slide 9+10

Q69.Sketch the connection diagram of combinational protection scheme that contains two over

current relays and one earth fault relay to provide phase to phase and phase to earth protection.

Slide 11

Q70.How will you adjust definite minimum time point on relay curve?

2.8  Materials/replacement parts required to solve problems are sourced and obtained in accordance with established procedures.

2.9  Effectiveness of the repair is tested in accordance with established procedures.

2.10  Apparatus is reassembled, finally tested and prepared for return to service.

Ref-Advanced Diploma in Electrical Engineering Exercises Page 126)

When more power loads are connected to transmission line, the current protection system needs to be modified. The following questions and activities provide this competency component.

(23) Transmission line protection

Slide 1

Q23.Sketch transmission line differential protection

Slide 2+3

Q24.Sketch the modification diagram for transmission line protection with differential relay.

--------------------------------------------------------------------------------------------------------------------------------------

(24) Distance relay, pilot wire with differential three phase line protection

Slide 1

Q25.Explain the operation of distance relay

Slide 2

126

Q26.Explain the operation of distance relay with sketch

Slide 3+4

Q27.Sketch the characteristics curve of distance relay

Slide 5+6

Q28.Explain the zone protection of distance relay.

Slide 7+8

Q29.Sketch the protection diagram of distance relay with operating & restraining voltage and

current.

2.11  Unexpected situations are dealt with safely and with the approval of an authorised person.

As per 1.3

2.12  Problem solving activities are carried out without damage to apparatus, circuits, the surrounding environment or services and using sustainable

energy practices.

As per 2.5

Location of Evidences (Table 1)

3.Completion and report for problem solving in energy supply network equipment

  - OHS work completion risk control measures and procedures are followed.

As per 1.3

3.2  Reusable, faulty or worn components are tagged and dispatched for repair to maintain adequate spares.

3.3  Maintenance work activities are documented in accordance with established procedures.

POWER SYSTEM PROTECTION COMMISSIONING PROJECT

The above diagram is Incoming HV supply system for a Cement Factory. It contains Star –Delta Transformer, Interchange switches for switching 2 supply, sketch of protective relay system with trip circuit and outline for measuring instruments.

(1) Develop Detail installation diagram that contain appropriate protection instruments and measurement instruments

(2) Recommend appropriate specifications for protection and measuring instruments for power supply requiring 500Kw for the factory.

By answering the following questions, the concepts for the above project can be highlighted

Ref-Advanced Diploma in Electrical Engineering Exercises Page 125)

(19) Three phase differential relay

Slide 1

Q17.Sketch three phase star/ delta transformer protection with differential relay.

125

Slide 2

Q18.Explain the setting of differential relay.

-------------------------------------------------------------------------------------------------------------------------------------

(20) Connection of main transformer, CT , directional relay

Slide 1+2+3

Q19.Sketch the combined earth fault and differential protection for three phase star/ delta

transformer.

www.electricaldiploma2013.webs.com

Work performance + Practical Instruction Back up

Click   HERE to download practicals

http://www.filefactory.com/file/cf88135/n/Practical.zip

Refer Power System Practicals

Part 1: Operational Study

| Lab No | Name of Practical | Equipments | Assessment |
| --- | --- | --- | --- |
|  | # Group 1 Power & Line |  |  |
| EP1 | Receiving end voltage comparison between short/ medium and long transmission lines | distribution system types | Circuit interpretation, connection, data collection, calculation, graph sketch, report presentation, conclusion |
| EP2 | Long transmission line PI equivalent circuit | overhead systems | As above |
| EP3 | Long transmission line T equivalent circuit | distribution system types | As above |
| EP4 | Transmission line efficiency/ Transformer effect on line efficiency | energy metering • demand meters | As above |
| EP5 | Reactive power and power factor improvement | energy metering • demand meters | As above |
| EP6 | PF effect on line current | energy metering • demand meters | As above |
| EP7 | Corona Video | • surge protection | Report presentation, conclusion |
| EP8 | Phase sequence measurement |  | Competency assessment |
|  | # GROUP 2- Protection equipments |  |  |
| EP9 | Connection of relay protection scheme & protective equipments by using one line diagram (Circuit interpreting & connection competency development without electrical supply) | protection equipment and systems | Competency assessment |
| EP10 | Current transformer & potential transformer connection & ratio test | current transformers • potential transformers | Circuit interpretation, connection, data collection, calculation, graph sketch, report presentation, conclusion |
| EP11 | Over current relay characteristics | protection equipment and systems • over-current protection | Circuit interpretation, connection, data collection, calculation, graph sketch, report presentation, conclusion |
| EP12 | Electronic relay test | conventional relays • electronic relays | As above |
| EP13 | Study of various protective relays used in industry through trade references | • earth fault protection • differential protection busbar protection • surge protection • conventional relays | Research, report presentation |
|  | Group 3- Supply System |  |  |
| EP19 | Underground cable capacitance test | underground systems | Circuit interpretation, connection, data collection, calculation, graph sketch, report presentation, conclusion |
| EP20 | High tension line design | • overhead systems | Design project |
| EP21 | Line insulator test & capacitance grading | • overhead systems | Circuit interpretation, connection, data collection, calculation, graph sketch, report presentation, conclusion |
| EP22 | Voltage profile chart of distribution system | • voltage regulation equipment • on load tap changers | As above |
| EP23 | Load centre-Power loss comparison | • distributor equipment | As above |
| EP30 | Transformer polarity test | • distributor equipment | As above |
| EP42 | Maximum power transfer theorem with power circuit | • load control | As above |
| EP43 | Load flow study | • load control | As above |
| EP45 | Trade reference study, switch board, busbar, insulator, circuit breakers | reclosers / sectionalisers. | As above |

## 2.10  Methods for dealing with unexpected situations are selected on the basis of safety and specified

## work outcomes.

## 2.11  Diagnosis and rectification activities are carried out efficiently without unnecessary waste of materials or damage to system and the

## surrounding environment or services and using  sustainable energy practices.

General faults including: open-circuit; short-circuit; incorrect connections; insulation failure; unsafe condition; apparatus/component failure; related mechanical failure for the equipments in the range

(2)Explore some of the faults in power system/ energy supply that can be rectified only by utilizing para-professional knowledge background and how the arranged simulated practical can provide the hand on experience and work performance for the students and how it is different from the performance only based on trade level activities.

In range of performance, it outlines the real equipments used in the industry. There will be the arguments that the setting of practical in lab room only includes rheostat, resistor, varic, capacitor etc. How it meets the outlined competencies?

To exactly find out and rectify the faults in energy supply system , the tasks and complexity level more than the trade level- (check the continuity, check the connection, visual inspection, testing and measurement )will be included.

The following is the various power system faults which I draw out from my power engineer work records  that the technical knowledge higher than trade level is required to successfully rectify the fault and determine the appropriate solutions. In the table, I summarize how the fault is , caused, background theory, how the person who knows the theory will do, how the person who does not know the theory will do and how my simulated practical / and practical related background theory will assist to develop the fault finding skill.

| Typical fault | Cause | Related Theory | How the person who does not know the theory will do | How the person who knows theory will do | Name of simulated practical | How to develop the skill |
| --- | --- | --- | --- | --- | --- | --- |
| (1)In reticulation system, there is abnormally different in voltages | Abnormal resistance. Wrong cable selection. Abnormal circuit configuration | Voltage profile chart. | May give he other idea to change the load | Measure voltage, sketch the voltage profile chart. Then identify the portion of the circuit. | EP 23 Voltage profile chart | Develop the analytical skills to identify the fault point |
| (2)Line conductor slips from the pin insulator | Line deviation is too high, combination of wind, conductor tension will take away the conductor from pin insulator | Line deviation angle calculation | Will reinstall the line. After some period, he same thing will happen again | Will examine line deviation angle. Tension, wind force. Will rearrange the line or provide shackle insulator | Theory instruction. Line deviation | Develop the problem solving skill on line construction. |
| (3)Conductor sag too low. Hit by traffic and then broken | Sag calculation. Wrong tension, safety factor, weight | Sag/ line design | Pull up the cable. After some time, it will fall again | Will examine the related parameters and find the way | EP 20 High Tension Line Design | Develop the skill on line design and to know the technical factors for sag. |
| (4)Discharge current flows out from underground insulator and cause the injury | UG cable capacitance. Charging current | UG Cable capacitance test | Will think about current flow, leakage etc. | Will examine the UG cable capacitance and produce the procedure for discharging | EP 19 Underground cable capacitance test | Develop the skill in UG cable testing focus on capacitance and estimate the amount of charging current |
| (5)Line pole broken without natural disaster | In appropriate pole strength | Pole mechanical design | Will erect the pole. Some time after, broken gain | Will examine he tension, wind force, conductor weight, then will calculate the pole strength and select appropriate diameter of pole and appropriate pole material | Pole mechanical design lesson + EP 20 High tension line design | Develop the skill on line design and to know the technical factors for pole. |

- Complete and report fault diagnosis and rectification activities.

3.1  OHS work completion risk control measures and procedures are followed.

3.2  Work site is made safe in accordance with established safety procedures.

As per 1.3

3.3  Rectification of faults is documented in  accordance with established procedures.

3.4  Appropriate person or persons notified, in accordance with established procedures, that the system faults have been rectified.

| Fault | Reason | Related theory | The person who does not know the theory will do | The person who knows the theory will do | Related Practical | Development of skill |
| --- | --- | --- | --- | --- | --- | --- |
| (6)There are too much power loss. Line efficiency is poor | If all connected loads are all right, wrong location of power station/ load centre | Load centre study | Will not take account on load centre | Will take account on load centre | EP23 Load centre power loss comparison | How the location of supply source affect line losses/ efficiency and % voltage regulation |
| (7)Problem with UG cable joint | Wrong method in UG cable joining | UG cable joining methods. Theory study |  |  | UG cable joining method in my prepared 7762 AA Electrical Distribution textbook | UG cable joining methods. Theory PLUS photographs |
| (8)Generator got motor action. Reverse power relay cuts off | Out of synchronism. Up to 180 degree out of phase | Synchronizing | Will neglect synchronism. Just run and switch on | Will focus on synchronizing process. Avoid reverse power relay operation | Synchronizing | Synchronism, generator parallel operation requirement practical knowledge development. |
| (9)Generator vibration/ hunting | Stability concept | System stability | Do not care on machine hunting. Will continue to run . As consequence, face the short life of bearing/ shaft | Will take care on transient and steady state system stability and prevent the hunting | Moment of inertia/ machine stability | Moment of inertia/ machine stability practical knowledge development. |
| (10)Relay operates on fault. But the system loss the synchronism | System stability/ critical fault clearing angle aspect. | System stability/ critical fault clearing angle | Do not care on the relay setting to provide both fault protection and maintain the system stability. Re-synchronize the generators when ever the relay operates | Will set the proper relay setting to maintain the stability | Critical fault clearing angle. Equal area criteria | Critical fault clearing angle. Equal area criteria practical knowledge development. |
| (11) Line reactive power too much. The equipment capacity is unnecessarily increased | Problem related to load flow | Load flow study | Will not take account on load flow concept. | Take account on load flow and optimize the loading | EP 42 Maximum power transfer theorem EP43 Load flow study | Develop the load flow concept and practical optimizing skill |
| (12)There is nothing wrong with the line but the transformer placed near the switch heat up and cooked | Switching surge | Switching voltage surge | Just replace the transformer. After some time, the same problem will be faced | Take account on switching voltage surge and plan tom install the surge diverter. | Switching voltage surge | Switching voltage surge practical knowledge development. |
| (13)Light radiated from the power line. Too much power loss and high interference to telecom line | Corona | Corona study | Will consider the ACT OF GOD | Will find the way to reduce corona such as application of hollow conductor to increase diameter of conductor to raise the critical voltage level | EP 7 Corona video | How corona occurs and find the way to prevent . |
| (14) Control telecommunication for power line down, no relay operates | Application of telecommunication system in power system operation | Application of telecommunication system in power system operation 7762AG Power System Operation | Will not be aware of the role of telecommunication system | Will check the function of telecom equipment for power system control and protection and perform the preventive maintenance | Application of telecommunication system in power system operation | Web based control/ IP based control and telecomm: concepts practical knowledge development. |
| (15)Too much flickering of lamps | Harmonics | Harmonics in power system | Will not know what happens | Will check the harmonics source/ increase the size of neutral wire to allow the harmonics current flows | Harmonic source scope observation | Development of identifying the harmonics |
| (16)Lightning strike | Lightning arrester | Lightning arrester | Will reinstall LA. But not sure it will be safe or not. | Will check the coverage provided by lightning arrester | Lightning arrester study | Lightning arrester practical knowledge development. |
| (17)Earth fault/ earth leakage can not be protected | Grounding in power system | Grounding in power system 7762AE Power System Protection | -- | Will measure the ground resistance, will implement the additional ground connections | Power system grounding study | Power system grounding practical knowledge development. |
| (18)Occurance of over current | Over current protection | Over current relay 7762AE Power System Protection | Will not exactly know how to set/ adjust the over current relay | Will set/ adjust the over current relay | EP11 Over current relay characteristics | Practical skill development in over current relay |
| (19)Earth leakage fault | Earth leakage protection | Earth leakage protection 7762AE Power System Protection | Will not exactly know how to set/ adjust the earth leakage relay | Will set/ adjust the earth leakage relay/ CT arrangement | CT arrangement for earth leakage fault & fault in protected zone | Practical skill development in earth leakage fault protection |
| (20)Transformer protection | Differential relay | Differential relay | Will not exactly know how to set/ adjust the differential relay | Will set/ adjust the differential relay | CT arrangement for fault in protected zone | Practical skill development in differential protection |
| (21)Line is protected by differential/ over current relay. But it is not effective when the load are fed from some part of the line | Distance relay | Distance relay | Will not exactly determine the reason why and how to change the protection system | Will change the protection system and will calculate earth fault impedance | Earth fault calculation | Problem solving skill development in earth fault calculation |
| (22)Fault happens but the relay can not provide the effective protection | CT/ PT ratio for relay | Relay protection scheme | Will not exactly determine the reason why and how to change the protection system | Will adjust CT PT ratio at the simulated fault situation and will adjust the relay setting appropriately | EP9 Connection of relay protection scheme & protective equipments by using one line diagram (Circuit interpreting & connection competency development without electrical supply) EP10 Current transformer & potential transformer connection & ratio test | Practical skill development in CT PT ratio adjustment |
| (23) I accidently open the CT secondary and it got explosion | Current transformer | Current transformer |  | Will make sure not to open circuit the CT secondary | EP10 Current transformer & potential transformer connection & ratio test | Develop the skill on CT/ PT connection & applications. |
| (24) we use old type gravity relay, it does not provide the effective protection | Restrainting system of relay | Relay types & characteristics |  | Will make sure to correctly arrange the relay position | EP13 Study of various protective relays used in industry through trade references | Knowledge development on various protective relays used in industry through trade references |
| (25) Relay operates at wrong current | Operation/ setting of relay | Relay types & characteristics | Trial error approach will be used | Will make sure to correctly arrange the relay setting | EP11 Over current relay characteristics | Practical skill development in over current relay |
| (26)In power transformer protection. Transformer is Star/Delta connection. All relay settings are correct. But relay wrongly operates. I checked all continuity. Every thing all right | Transformer Star Delta & relay star/delta matching | Star delta vector diagram. Transformer star side –Relay delta & transformer delta—Relay star | Will not know what happens and how to rectify the fault | Will check the connection and will consider the vector difference causes the wrong operation | EP10-CT & PT connection/ ratio check | Practical skill development in CT/PT Connection |
| (27)Regulator is set to meet the system voltage condition. But later time, it is blown out | Voltage ratio/ regulator setting | Voltage regulator | Will emphasize in solving the problem for a short moment. Will not consider the long term impact | Will consider whether the setting to upgrade the voltage will impact on future system voltage change | EP22 Voltage profile chart of distribution system | The skill training to develop the judgment of voltage level and future impact |
| (28)Fault spread from one busbar to another busbar | Busbar arrangement/ sectionalization | Busbar arrangement | Will assemble he busbar to install the equipment, will not consider how the arrangement can contribute the spread of fault | Will consider the way to insert section circuit breakers | Busbar layout/ arrangement study | Busbar arrangement sketch/ plan practice development |
| (29)Equipment suffers over voltage and blown out after the capacitor value is changed for PF improvement | Inappropriate capacitor setting. Cause of overvoltage. Vector diagram | PF improvement/ Capacitive reactance effect on load | Will only see the way to improvement the PF. Will not know the consequences | Will posses the knowledge of capacitor impact on load voltage and will take account on optimal setting of capacitor value | EP5-capactance effect on line EP6-PF Improvement | PF improvement method is judgment with capacitor effect causes over voltage. This skill is trained. |
| (30)Directional relay does not work to protect the reverse power flow | Directional relay operation | Study on directional relay. |  | Wrong connection to direction coil will be identified | EP 13 Protective relays used in industry | Guide to acquire the relevant technical knowledge |
| (31)Voltage flashing over capacitor string | Capacitor string | Study on capacitor string | Will change the capacitor string | Will provide the preventive protection such as arcing horns OR take account on line capacitor grading | EP21 Line insulator capacitance test | Develop the skill to measure line capacitor value . Capacitance grading. |
| (32)Circuit Breaker itself is blown out | Circuit Breaker capacity | Study on capacity of circuit breaker | Will change CB. After sometime, it will blow up again. | Will consider the CB capacity & possible over current developed in line fault | EP13 Relay & CB used in system Fault current | Develop the skill in fault current estimate and choosing CB capacity |
| (33)CB too hot and meltdown | CB capacity/ Arc development | Study on capacity of circuit breaker/electric arc | Will change CB. After sometime, it will blow up again. | Will consider the CB capacity & possible over current developed in line fault Will consider the arc extinguishing methods | EP13 Rely & CB used in system Fault current | Develop the skill in fault current estimate and choosing CB capacity |
| (34)Need to expand the line in emergency. I am only in-charge | Line design | Line design project | Will not know how to design a line | Will utilize references/ methods to design and construct the line | 7762AA Project-Over head line design | Line electrical & mechanical design practice development |
| (35)HV current flows into LV line | Separation between HV & LV line | Rules & regulations related to line | Will not know the regulation | Will apply the regulation in real wok | 7762AA Line pole/ cross arm design and conductor arrangement | Line electrical & mechanical design practice development |
| (36) Line wire fracture | Sag calculation | Sag calculation/ minimum cable size | Reinstall the line wire. Like part to like part replacement is applied, will use the same size of cable. After sometime, line will break gain | Will consider allowable tension/ minimum conductor size | 7762AA Project-Over head line design | Line electrical & mechanical design practice development |
| (37)Electronics equipment used for line protection is blown up | Voltage surge | Signal condition sub system. Surge filter | Will replace the electronic board. But the same fault happens again | Will consider the cause of surge. Surge filter / absorber/ diverter will be installed | 7762AE Line surge/ application of electronic control system | Develop the skill in line surge/ electronic control. |
| (38) Receiving end voltage is greater than the sending end | Capacitance effect on long line | Long line 7762AG Power System Operation | Will think that the equipments are designed to operate at the sending end voltage level, it will be enough | Will consider the line configuration and will provide the appropriate arrangement for over voltage caused by capacitance effect on long line. | EP2/EP3 Long Line PI & TEE equivalent circuits | Develop the practical skill in determination of possible voltage rise in simulated line model. |
| (39)Can not run the generators in parallel | Synchronism problem | Synchronizing | Will not properly know the synchronism | Will consider the synchronism | Alternator parallel operation- Procedure | Develop he knowledge in synchronizing |
| (40) Over current relay is provided to protect the system but it does not work when the ground fault occurs | Characteristics of relays | Relay types and characteristics | Will think that one relay will protect everything | Will select the appropriate relay for appropriate place and protection task | EP13 Study of various protective relays used in industry through trade references | Knowledge development on various protective relays used in industry through trade references |

| Method of delivery | Method of collection of evidence |
| --- | --- |
| 7-Face to face 6-Electronic # Key for delivery mode 1-On the job 2-Simulated 3-Blended 4-Self paced 5-Distance 6-Electronic 7-Face to face 8-Other # Detailed explanation Face to face class teaching + Online supplement multimedia notes Evidence Part 1- Evidence of teaching & learning Plan for concurrently delivery www.powerlearning1.zoomshare.com Both digitised notes + multimedia notes including audio files Notes in USB ( Available on request) #### Part 2- Evidence of lesson planning - Delivery & assessment matrix excel form - Semester plan - Students study progress plan ( Available on request) | A,B,D,E,F,G,L Key for Methods for Collecting Evidence: A-Assignment B-Written Task C-Role play D-Exam E-Oral questioning F-Simulation G-Observation H-Work based I-Portfolio J-Self assessment K-Case study L-Practical demonstration M-Project N-Training Record O-Other ## Detailed explanation A+B-Test 1, 2, 3, 4 E-Oral question in practical class F-Simulated practical for line & power system comprising mathematical equations & functions G-Observe the student’s performance in practical class L-Student practical performance result + report preparation ## Evidence Attached ### Part (1)- Test questions 2 tests ### Part (2)-Evidence of students participation - Signed attendance sheet - Signed Test attendance sheet - Sample answer paper & practical report Either hard or scanned copy ( Will be available on request within 6 months of the assessment event - EBS attendance & grade record |

| 1 | On the job | 2 | Simulated | 3 | Blended | 4 | Self-paced (facilitated) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5 | Distance | 6 | Electronic | 7 | Face to Face | 8 | Other (Please specify) |

| Key for Methods for Collecting Evidence: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | Assignment | B | Written task | C | Role play | D | Exam |  |
| E | Oral questioning | F | Simulation | G | Observation | H | Work based |  |
| I | Portfolio | J | Self assessment | K | Case study | L | Practical demonstration |  |
| M | Project | N | Training Record Book | O | Other (Please specify) |  |  |  |

Location of Evidences (Table 1)

ASSESSMENT SCHEDULE

| Performance Criteria | Assessment 1 Practical |  | Assessment 2 Theory |
| --- | --- | --- | --- |
|  | Continuous Observation | Written Assessment as part of Practical | Written Assessment |
| 1.1 |  | X |  |
| 1.2 |  | X |  |
| 1.3 |  | X | X |
| 1.4 |  | X | X |
| 1.5 |  | X | X |
| 1.6 |  | X | X |
| 2.1 |  | X |  |
| 2.2 |  | X | X |
| 2.3 |  | X | X |
| 2.4 |  | X | X |
| 2.5 |  | X | X |
| 2.6 |  | X | X |
| 2.7 |  | X | X |
| 2.8 |  | X | X |
| 2.9 |  | X | X |
| 2.10 |  | X | X |
| 2.11 |  | X | X |
| 2.12 |  | X | X |
| 3.1 | X | X |  |
| 3.2 | X |  |  |
| 3.3 | X |  |  |
| EKAS Assessment |  | X | X |

POWER SYSTEM Youtube video Lessons to provide the sufficient EKAS

G015/ IS67+68+ IS74

Page        196       to        231                of  http://www.filefactory.com/file/cf9bf8f/n/Video_Lessons.pdf

Power System (1)

G015(AA)Lesson 1-Distribution system.zip

http://youtu.be/VuzjXkRx4UI

G015(AA)Lesson 2-Demand factor.zip

http://youtu.be/cUGbxhBT-Dc

http://youtu.be/DCCl4cO3Vu8

G015(AA)Lesson 3-Sag.zip

http://youtu.be/1s496h-Iuu8

G015(AA)Lesson 4-OH Line mechanical design.zip

http://youtu.be/T0BnyqV9T6E

http://youtu.be/hu1TrUv2_OY

G015(AA)Lesson 5-UG Cable.zip

http://youtu.be/hHCLzMnVmT0

http://youtu.be/A5AieaBBZHo

G015(AA)Lesson 6-Voltage control.zip

http://youtu.be/y1vTM5fvfyU

http://youtu.be/Z9HBGsVgymA

G015(AE)Lesson 1-Power system protection scheme.zip

http://youtu.be/ihpd3cDAhBU

http://youtu.be/EGXkLRM2L9M

http://youtu.be/zOIUYQ7OJfs

G015(AE)Lesson 2-Differential relay.zip

http://youtu.be/2iW0oEScMsw

G015(AE)Lesson_3-Over_current_&_earth_fault_protection.zip

http://youtu.be/hvGjdO9jEhk

G015(AE)Lesson 4-Three phase differential relay.zip

http://youtu.be/2iW0oEScMsw

http://youtu.be/VuzjXkRx4UI

http://youtu.be/2iW0oEScMsw

G015(AE)Lesson 5-Current time grading.zip

http://youtu.be/r0qkLrmkKsM

G015AE Lesson 6

http://youtu.be/InsTLh7_N5k

G015(AE)Lesson_7-CT_PT.zip

http://youtu.be/ZF_y65xsM_M

G015(AE)Lesson 8-Distance relay.zip

http://youtu.be/NKzMVquFLu8

http://www.filefactory.com/file/c386a2e/n/G015_AE_Lesson_8-Distance_relay.zip

G015(AE)Lesson 9-Telecom in power protection.zip

http://youtu.be/9C6ogqZAKRg

http://youtu.be/XRpffA6hU_U

http://youtu.be/X-kz3cyL9fU

G015(AG)Lesson 1-Stability.zip

http://youtu.be/fUyNqcXtBXg

G015(AG)Lesson 2-Generator load sharing.zip

http://youtu.be/A-t7XH4rK4M

http://youtu.be/OTsis_KIRuk

http://youtu.be/8j1nD9nY2hU

G015(AG)Lesson 3-Power Flow.zip

http://youtu.be/0OzT4Pol-Jc

http://youtu.be/fK0wcaTY_rw

G015(AG)Lesson 4-IP based system.zip

http://youtu.be/ve5O8K9fL7k

G015(AG)Lesson 5-Surge in power system.zip

http://youtu.be/6WkezTcOzX4

G015(AG)Lesson 6-CTPT Harmonic filter.zip

http://youtu.be/Uy7q9SsaOYs

G015(AG)Lesson 7-Short circuit in alternator.zip

http://youtu.be/b-46Kvn8kJI

G015(AG)Lesson 8-Corona.zip

http://youtu.be/XYGRAWOqzsc

G015(AG)Lesson 9-Power surge.zip

http://youtu.be/uzFS-otIn-g

http://youtu.be/IsZ_ccy630w

G015(AG)Lesson_10-Static_Var_Compensation.zip

http://youtu.be/y-of5oLojCU

G015(AG)Lesson 11-PF Control+Fuel cell.zip

http://youtu.be/AXbCcoQeLns

G015(AG)Lesson_12-Exercises.zip

http://youtu.be/nRGScOH9aSM

G037+G038+G039 Part 1/2/3+IS69

Page    232           to            270            of  http://www.filefactory.com/file/cf9bf8f/n/Video_Lessons.pdf

Power System (2)

G037+G038+G039 Lesson 1-Power Flow.zip

http://youtu.be/mzwGGXRTtvw

G037+G038+G039 Lesson 2-Site Earthing.zip

http://youtu.be/PATkXVBF9kc

http://youtu.be/H4Dj1K238BE

G037+G038+G039 Lesson 3-Power System Control Equipments.zip

http://youtu.be/JJczbYVWOoI

G037+G038+G039 Lesson 4-Auxiliary System+Harmonic.zip

http://youtu.be/5mDNHGFLA0c

G037+G038+G039 Lesson 5-Harmonic.zip

http://youtu.be/n41q4Rmz2p0

http://youtu.be/8CelGV5AElk

G037+G038+G039 Lesson 6-Harmonic Calculation.zip

http://youtu.be/NHSzu6HkOgI

http://youtu.be/fSLrPIC6Mho

G037+G038+G039 Lesson 7-Synchronous Generator Loading.zip

:http://youtu.be/jv1q7Mtg7Gs

http://www.filefactory.com/file/c39be2f/n/G037_G038_G039_Lesson_7-Synchronous_Generator_Loading.zip

G037+G038+G039 Lesson 8-Turbine Control+Power Line Earthing.zip

http://youtu.be/0CvgkmDE3Kw

G037+G038+G039 Lesson 9-Insulator.zip

http://youtu.be/l4jqs8MLBFA

http://youtu.be/TiQezIA9Z-c

G037+G038+G039 Lesson 10-Reliability of Power System.zip

http://youtu.be/tIUk3nc1IxE

G037+G038+G039 Lesson 11-Harmonic Reduction.zip

http://youtu.be/8dYX-11kRcc

http://youtu.be/A684Agej8-w

G037+G038+G039 Lesson 12-Grounding + Power Quality.zip

http://youtu.be/QQPUj3WXJnA

G037+G038+G039 Lesson 13-Power Quality.zip

http://youtu.be/feI7SCb_QTY

http://youtu.be/mcK2YhDsnr0

G037+G038+G039 Lesson 14-Harmonic Model.zip

http://youtu.be/dwWBOq-BsLY

G037+G038+G039 Lesson 15-Harmonic Losses in Transformer.zip

http://youtu.be/mwEJgEEgPVc

http://youtu.be/1A6FY5f5ijM

http://youtu.be/yLiOKy7uJj0

G037+G038+G039 Lesson 16-Reliability Improvement.zip

http://youtu.be/cn-CfDWnUN8

G037+G038+G039 Lesson 17-Preparation for emergency.zip

http://youtu.be/La7Xip8GI2I

G037+G038+G039 Lesson 18-Harmonic problems.zip

http://youtu.be/0Urnkee_

http://youtu.be/zM_Xcwckicw

G037+G038+G039 Lesson 19-Synchronous machine problems.zip

http://youtu.be/Lx2S-NATr20

G037+G038+G039 Lesson 20-Power Generation + Generator Control.zip

http://youtu.be/56Ks8sArQxc

G037+G038+G039 Lesson 21-Turbine Control+ Digital Excitation.zip

http://youtu.be/uCsvv18qKwQ

http://youtu.be/I4vCDI2CZS0

G037+G038+G039 Lesson 22-Power System Protection.zip

http://youtu.be/c6iXRwfCYBU

G037+G038+G039 Lesson 23-Switch Gear.zip

http://youtu.be/DDpbzgNYTiM

http://youtu.be/2cl-nOdBNro

G040 + IS73

Page    271           to        284                of  http://www.filefactory.com/file/cf9bf8f/n/Video_Lessons.pdf

Power transformer

G040 Lesson 1 Power transformer rating 1.zip

http://youtu.be/qjWJVQAh_jA

G040 Lesson 1 Power transformer rating 2.zip

http://youtu.be/JonzO8JD-k4

G040 Lesson 2 Open circuit short circuit test.zip

http://youtu.be/Ru-KlKv40OY

G040 Lesson 3 Transformer regulation.zip

http://youtu.be/t6IZMwMj-B4

G040 Lesson 4 Power transformer connection.zip

http://youtu.be/iig8PISDN1I

G040 Lesson 5 Maximum efficiency.zip

http://youtu.be/Qa7l0eHTWTU

G040 Lesson 6 Transformer parallel operation.zip

http://youtu.be/dkRxoaozrOk

http://youtu.be/Sz5QY727w-8

G040 Lesson 7 Harmonic in transformer.zip

http://youtu.be/_YOlWb3e574

G040 Lesson 8 Transformer problem + auto transformer.zip

http://youtu.be/0KCscbCIUjk

G040_Lesson_9_Transformer_rating_cooling_connection_tap_changing.zip

http://youtu.be/d3XHm-wguzQ

http://youtu.be/XwiIkZnKFqQ

http://youtu.be/uOHBk840Bhw

G040 Lesson 10 Phase shift transformer.zip

http://youtu.be/7aWhg9DIoWI

G042+IS71

Page      285         to        307                of  http://www.filefactory.com/file/cf9bf8f/n/Video_Lessons.pdf

Transmission Line

G042 Lesson 1-Transmission line introduction.zip

http://youtu.be/DrOOgcKeaL4

G042 Lesson 2-DC Line+Line reflection.zip

http://youtu.be/jvVdecp-clk

G042 Lesson 3-Power line calculation.zip

http://youtu.be/3TgVt67DhvY

http://youtu.be/QT6aqsaM7a0

http://youtu.be/WxjQIkdJjQ8

G042 Lesson 4-Line model+Economic aspect.zip

http://youtu.be/1HRdGZXp_-w

G042 Lesson 5-Time value of money+Line reflection.zip

http://youtu.be/n9mupLQWANY

http://youtu.be/YdfiX2gL-3c

G042 Lesson 6-Line matching+Wave guide.zip

http://youtu.be/1WyP5_Cek40

G042 Lesson 7-Wave guide.zip

http://youtu.be/BuGtjZ3QBXk

http://youtu.be/pftevsnbl0w

G042 Lesson 8-Microstrip line.zip

http://youtu.be/eINq1kKuiec

G042 Lesson 9-Per unit value of line.zip

http://youtu.be/66Y-Lm3EntI

G042 Lesson 10-Line constants.zip

http://youtu.be/2XYnZZ-zXII

G042 Lesson 11-Smith chart.zip

http://youtu.be/dv-NQh4vlrg

http://youtu.be/KfM8XZd9Wqc

http://youtu.be/3NYVQvW8-Nk

http://youtu.be/5qBwLsbtfTA

http://youtu.be/ViamcvqAy_I

http://youtu.be/j_nx9n7mGec

http://youtu.be/d53B3-zV2ec

G042 Lesson 12-Four terminals network.zip

http://youtu.be/HCO4P1qrPbA

G042 Lesson 13-Exercises.zip

http://youtu.be/LeyJf1PhpCY

Power References

http://electricaldiploma2013.zoomshare.com/files/powerreference.htm

Advanced Diploma in Electrical Engineering Exercises

Click HERE