## Slide 1
Lesson 7
Chapter 21
Transformers
Sections
21.10 Auto transformers
21.11 Instrument transformers
21.12 Insulation resistance test

## Slide 2: 21.10 Auto-transformers
An auto-transformer has an electrical connection between its primary and secondary windings, and can be either step down or step up
Notes: Figure 21.39

## Slide 3: Variable auto-transformer
A variable autotransformer (variac) provides a variable output voltage determined by the position of the wiper
Notes: Figure 21.40

## Slide 4: 21.11 Instrument transformers
Instrument transformers fall into two categories: voltage transformers (VT) and current transformers (CT).
Instrument transformers are used to provide a means of measuring and monitoring high voltages and currents that are otherwise impossible to measure.

## Slide 5: Voltage transformers
Three-phase VT in a 33 kV substation, monitoring the bus voltage to a power transformer
Notes: Figure 21.41

## Slide 6: Voltage transformer connections
A three-phase VT is usually connected in star–star with the neutral points earthed
Notes: Figure 21.42

## Slide 7: Current transformers
CTs are arranged one per phase, and vary in size, voltage and current ratings
Notes: Figure 21.43

## Slide 8: Current transformer connections
CTs providing information to a protection system in a three-phase double star capacitor bank
Notes: Figure 21.44

## Slide 9: 21.12 Insulation resistance test
An insulation resistance tester applies a high DC voltage to the equipment under test and displays a resistance reading. Tests on a transformer are between:
HV and LV windings
HV winding and earth
LV winding and earth
HV winding and both the LV winding and earth
LV winding and both the HV winding and earth.

## Slide 10: Typical insulation resistance tests (IRT)
Measuring the insulation resistance between transformer windings with a 10 kV insulation resistance tester
Notes: Figure 21.45

## Slide 11: Chapter summary
An auto-transformer has a single winding shared by the primary and secondary terminals. They can be step up, step down or variable (variac) and they do not isolate the HV side from the LV side.
Instrument transformers are used to measure and monitor very high values of voltage and current. They are used in metering, protection and control systems.
An insulation resistance test measure the leakage resistance between transformer windings, and the windings and earth.

## Slide 12: Equation summary
V = 4.44 NfΦmax
where:
V = RMS value of the induced voltage,
N = number of turns on the coil
f = frequency of the voltage in hertz
Φmax = maximum magnetic flux in webers.

## Slide 13: Equation summary (2)
where:
transformer voltage ration
current ratio
turns ratio.

## Slide 14: Equation summary (3)
where:
VNL = unloaded secondary voltage
VFL = loaded secondary voltage.

## Slide 15: Equation summary (4)
efficiency:
PIN = V1I1λ1, POUT = V2I2λ2 (single-phase)
PIN = √3V1I1λ1, POUT = √3V2I2λ2 (three-phase)

## Slide 16: Equation summary (5)
% transformer impedance:
prospective short-circuit current:
Two transformers in parallel: