## Slide 1
Lesson 1
Chapter 21
Transformers
Sections
21.1 Introduction
21.2 The ideal transformer
21.3 The practical transformer

## Slide 2
UEENEEG006A
Solve Problems in Single Phase
& Three Phase Low Voltage Machines
Transformers (Static Machines) &
Rotary Machines (Motors & Generators)
Notes: Title

## Slide 3
04/02/19
11/02/19
18/02/19
25/02/19
04/03/19
11/03/19
18/03/19
25/03/19

## Slide 4
01/04/19
08/04/19
29/04/19
06/05/19
13/05/19
20/0519
27/05/19
03/06/19
17/06/19
10/06/19
Term Break
Notes: 10/06/19 is PUBLIC Holiday – Will need to fit 24.1 & 24.2 into one week

## Slide 5
NOTE: No practical for AC Machines Test #1
NOTE: No practical for AC Machines Test #1
04/03/19
25/03/19
13/05/19
17/06/19

## Slide 6
DC Theory
Formulae Sheets

## Slide 7
Electromagnetism & DC Machines
Formulae Sheets

## Slide 8
AC Theory
Formulae Sheets

## Slide 9
Transformers & Rotary Machines
Formulae Sheets

## Slide 10
Chapter 21
Transformers

## Slide 11: About this chapter
The transformer is an essential part of today’s power transmission and distribution. Transformer design still relies on the principles established over 100 years ago, including many of the construction techniques.
This chapter:
examines the operating principles of single and three phase transformers
describes some of the tests and measurements associated with transformers

## Slide 12: Contents
21.1 Introduction
21.2 The ideal transformer
21.3 The practical transformer
21.4 Transformer operation
21.5 Voltage regulation
21.6 Transformer performance
Notes: 12 Sections – 2 slides

## Slide 13: Contents (2)
21.7 Transformer connections
21.8 Transformers in parallel
21.9 High voltage safety
21.10 Auto-transformers
21.11 Instrument transformers
21.12 Insulation resistance test

## Slide 14
Lesson 1
Chapter 21
Transformers
Sections
21.1 Introduction
21.2 The ideal transformer
21.3 The practical transformer

## Slide 15: 21.1 Introduction
A transformer changes an alternating voltage from one value to another.
Because of the transformer, AC power is generated at one voltage, transformed up to a much higher voltage for transmission, then transformed down to voltages such as 400 V/230 V for domestic use.
Transformers are found in many electronic appliances, battery chargers, and mains-powered test equipment.

## Slide 16: Power transformers
The power transformer transforms an incoming 66 kV supply to 11 kV. The auxiliary transformer provides 400 V from an 11 kV supply
Notes: Figure 21.1

## Slide 17: 21.2 The ideal transformer
Transformers typically have a laminated iron core and two or
more windings
Notes: Figure 21.2

## Slide 18: Operating principles
Transformers operate on the principle of mutual inductance: when one coil induces voltage in another coil.
When the primary winding of a transformer is connected to an AC supply, the current flowing through the winding produces an alternating magnetic flux in the core.
If the supply voltage is sinusoidal, the current and the flux produced by the current are also sinusoidal.
A sinusoidal induced voltage is produced in all windings on the transformer, including the winding connected to the supply

## Slide 19: Operating principles (2)
The current flowing in the primary winding of a transformer increases when a load is connected to the secondary and energy is transferred from the supply to the load
Notes: Figure 21.3

## Slide 20: Operating Principles - Video
What is a Transformer And How Do They Work?
https://www.youtube.com/watch?v=vh_aCAHThTQ
https://youtu.be/Cx4_7lIjoBA
https://www.youtube.com/watch?v=agujzHdvtjc

## Slide 21: Transformer circuit symbols
Notes: Figure 21.4

## Slide 22: Induced voltage value
For sinusoidal waveforms, the RMS voltage induced in the primary or secondary windings of a transformer:
where:
V = RMS value of the induced voltage
N = number of turns on the coil
f = frequency of the voltage in hertz
Φmax = maximum value of the magnetic flux in webers.

## Slide 23
Example 21.1
A transformer has 500 turns on its primary winding () and 100 turns on the secondary (). The maximum value of the flux in the core is 2.16 milliweber and the frequency is 50 Hz. Calculate the voltage induced in the:
Primary winding (),
Secondary winding ().
Values:
 | 500 turns |  | 50 Hz
 | 100 turns |  | 2.16 mWb
 | 500 turns |  | 50 Hz
 | 100 turns |  | 2.16 mWb

## Slide 24: Transformation ratio
Mathematical relationship between the primary and secondary voltages and the primary and secondary turns:

## Slide 25: Transformation ratio
Mathematical relationship between the primary and secondary voltages and the primary and secondary turns:
where:
turns ratio

## Slide 26
Example 21.2
A transformer has 960 turns on its primary winding () and 48 turns on the secondary (). Calculate the:
Turns ratio of the transformer,
Secondary voltage when 230 V rms is applied to the primary.
Values:
 | 960 turns |  | 230 V rms
 | 48 turns |  | 
 | 960 turns |  | 230 V rms
 | 48 turns |  | 

## Slide 27: Power ratio
The Power relationship between the primary and secondary in an IDEAL Transformer:
where:
Expressed in Volt-Amps.
Why?
Notes: Expressed in Volt-Amps.
Why? Because the LOAD is unknown!!

## Slide 28
Rearrange:
Therefore:

## Slide 29: Current ratios
Mathematical relationship between the primary and secondary currents and the primary and secondary turns:
where:
current ratio
turns ratio

## Slide 30
Example 21.3
The transformer in Figure 21.5 has 720 turns on its primary winding () and 100 turns on the secondary (). The transformer primary is connected to 230 Vac and the secondary is connected to a 30Ω load. Calculate the:
Secondary voltage,
Secondary current, and
Primary current.
Values:
 | 720 turns |  | 230 V rms
 | 100 turns |  | 30Ω
 | 720 turns |  | 230 V rms
 | 100 turns |  | 30Ω
Figure 21.5

## Slide 31: Summing up
In an ideal transformer:
the voltage ratio equals the turns ratio
the current ratio is the inverse of the voltage (or turns) ratio
there are no losses and the transformer consumes no power.

## Slide 32: 21.2 The practical transformer
All transformers experience some losses, which means a transformer draws a primary current when it is not connected to a load.
It also means the transformer will generate heat during operation.
The aim of transformer design is to minimise the losses, which are made up of winding (copper) losses and core (iron) losses.

## Slide 33: Core construction
Transformer core design aims to minimise magnetic leakage, hysteresis loss and eddy currents
Notes: Figure 21.6

## Slide 34: Single-phase transformer cores
The core-type transformer is commonly used in power transmission and distribution
Notes: Figure 21.7

## Slide 35: Shell type transformer core
The shell-type transformer has its windings wound around the centre limb of the core
Notes: Figure 21.8

## Slide 36: C-core
C-cores are used in both core-type and shell-type transformers
Notes: Figure 21.9

## Slide 37: Toroidal core
Toroidal transformers have a low level of radiated magnetic field and a high efficiency
Notes: Figure 21.10

## Slide 38
Transformer windings
Winding arrangements depend on the voltage and power ratings
of a transformer
Notes: Figure 21.11

## Slide 39: Transformer ratings
Transformers are rated in apparent power which is expressed as a VA (volt-amps) rating.
This indicates the maximum current the low voltage winding can safely provide at its rated terminal voltage, regardless of power factor.
The current rating depends on the rate at which heat can be dissipated by the transformer.

## Slide 40
Example 21.4
The 2 MVA transformer in Figure 21.12 has two secondary windings of 10 kV and 400 V. How much current can the 10 kV winding provide if the 400 V winding is supplying 100 A to a load?
Values:
 | 2 MVA |  | 400 V
 | 10 kV |  | 100 A
 | 2 MVA |  | 400 V
 | 10 kV |  | 100 A
Figure 21.12

## Slide 41: Three-phase transformers
A three-phase power transformer is typically made up of three single-phase transformers with the coils on a common core
Notes: Figure 21.13

## Slide 42: Transformer cooling
Power transformers are usually cooled by circulating mineral oil through the windings, and cooling the oil by convection or forced air flow
Notes: Figure 21.14

## Slide 43: Transformer oil
The condition of transformer oil is indicated by its colour
Notes: Figure 21.15

## Slide 44: Summing up – practical transformer
Losses are made up of iron and copper (I2R) losses.
Losses cause heat which is removed in large transformers by circulating oil through the windings and core.
Eddy currents in the core are reduced by laminating the core.
Cores can be shell or core-type, power transformers are usually core-type, in some cases C-cores are used.

## Slide 45: Summing up – practical transformer (2)
Windings can be double-wound, side by side, or pancake, depending on the ratings of the transformer.
The volt-amp rating of the transformer determines the value of continuous secondary current the transformer can provide without overheating.
A three-phase transformer has a single multi-limb core with three single-phase windings.

## Slide 46
Practical Exercise 1
Transformer Ratios