## Slide 1
Lesson 4
Chapter 21
Transformers
Section
21.6 Transformer performance

## Slide 2: 21.6 Transformer performance
Two tests that can be done on a transformer that allow its performance to be evaluated are the open-circuit test and the short-circuit test.
From the results of these tests a number of important performance characteristics can be determined, such as the transformer’s efficiency, its impedance and prospective short-circuit current.

## Slide 3: Short-circuit test
A short-circuit test measures the copper losses in a transformer. V1 is slowly increased until the ammeters show the transformer’s rated full-load currents.
Notes: Figure 21.26

## Slide 4: Open-circuit test
An open-circuit test measures the iron losses in a transformer with a wattmeter. V1 is the transformer’s full rated voltage
Notes: Figure 21.27

## Slide 5: Efficiency
single-phase: PIN = V1I1λ1, POUT = V2I2λ2.
three-phase: PIN = √3V1I1λ1, POUT = √3V2I2λ2.
Notes: Figure 21.28

## Slide 6: All-day efficiency
To determine the all-day efficiency of a transformer, its input energy and output energy are measured over a 24-hour period.
where:
kWh = kW × time.

## Slide 7: Transformer impedance
The impedance of a transformer determines the amount of fault current that can flow in the windings should a short-circuit occur across its terminals.
If a transformer is to work in parallel with another transformer in a load sharing arrangement, it’s important that both transformers have the same impedance.
The impedance of a transformer is calculated from the measurements taken during a short-circuit test.

## Slide 8: Short-circuit test setup
When I2 equals the transformer’s full rated secondary current, the voltage at the primary (V1) is the transformer’s impedance voltage
Notes: Figure 21.26 (again)

## Slide 9: Calculating transformer impedance
The impedance voltage is the voltage required to cause rated current to flow though the impedance of the windings.
Percentage transformer impedance is the ratio of the impedance voltage (VSC) and the transformer’s rated voltage V multiplied by 100:

## Slide 10: Example name plate
Section of a 35 MVA 66 kV/11 kV power transformer nameplate showing its impedance as a percentage voltage value
Notes: Figure 21.29

## Slide 11: Prospective short-circuit current
The maximum value of a possible short-circuit current (ISC) in the low voltage winding of a transformer can be determined from its percentage impedance:
where:
Irated is the transformer’s rated secondary current.

## Slide 12: Summing up
Transformer voltage regulation is the change in secondary voltage divided by the no-load voltage. Multiplied by 100 gives % voltage regulation.
A tap changer is a switch that changes a transformer’s turns ratio (and therefore its secondary voltage) by selecting tappings on either the primary or secondary windings.
Distribution transformers usually have an off-load tap changer, transmission transformers have an on-load tap changer.

## Slide 13: Summing up (2)
An on-load tap changer has a complex switching arrangement that ensures current is maintained at all times to the load during a switching operation.
A short-circuit test measures a transformer’s copper losses. It also gives the voltage required to establish full-load current in the windings, which allows the transformer’s impedance to be calculated.
An open-circuit test measures iron losses of a transformer, which remain virtually constant regardless of load.

## Slide 14: Summing up (3)
efficiency:
single-phase: PIN = V1I1λ1, POUT = V2I2λ2.
three-phase: PIN = √3V1I1λ1, POUT = √3V2I2λ2.
% transformer impedance:
prospective short-circuit current: