## Slide 2
Chapter 23
Single-phase motors
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 3: About this chapter
<number>
Single-phase motors are used extensively and operate in a similar way to the three-phase induction motor, but have an additional winding to make them start.
This chapter:
looks at the various types of single-phase motors, including capacitor motors, shaded-pole motors and universal motors.
describes these motors, their protection requirements and typical faults.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 4: Contents
<number>
23.1 Single-phase induction motors
23.2 Capacitor motor
23.3 Shaded-pole induction motor
23.4 Universal motors
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 5: 23.1 Single-phase induction motors
<number>
A single-phase motor produces a pulsating magnetic field that holds the rotor stationary. It therefore needs an extra winding to make it rotate.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.1
Shows pulsating field with no rotation Demonstrate with motor.
Explain that turning by hand will cause induction into rotor and therefore the rotor will keep running.
If you disconnect two lines of a three phase motor it will run with reduced efficiency and torque.
Can be squirrel or wound and categorised as split phase, capacitor motors and shaded pole.
We will look at these individually.
Single phase motors with wound rotors have an armature & commutator like DC motors.

## Slide 6: Split-phase induction motor
<number>
A split-phase induction motor has two sets of windings,
The run winding - High inductance and a Low resistance
The start (auxiliary) winding – Low Inductance, High resistance
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.2
Explain
Run winding which has a large CSA and set deeper in the core which gives it a large phase angle in relation to the supply voltage. Approx example 50degrees
Start winding which has opposite characteristics and 25% less turns & set higher in the core, less of a phase angle approx example 20 degrees.
Overall phase shift between both currents is 30 degrees
The phaser sum of these currents causes an rotating elliptical magnetic field which provides enough torque to move the rotor.

## Slide 7: Centrifugal switch
<number>
Once the motor is at around 75% of its running speed, the start winding can be disconnected by a centrifugal switch.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.3
Demo with split phase motor and show you tube clip.
Start winding cannot be left running. Small gauge wire will burn out.
Connected in series with start winding.
Next slide shows diagram and current relay

## Slide 8: Circuit – split-phase induction motor
<number>
This circuit incorporates a centrifugal switch and circuit
This circuit has a motor start relay to switch the start (auxiliary) winding
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.4
Current relay energises with large inrush current and as motor speeds up current reduces and relay drops out, opening relay contact to start winding.
Relay can be positioned local or remote.

## Slide 9: Typical motor
<number>
A typical split-phase induction motor with a centrifugal switch in the start circuit
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.5
Step through components, next slide calculating speed.

## Slide 10: Split-phase motor characteristics
Synchronous speed of a split-phase motor:
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles.
<number>
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 11: Torque-speed curve
<number>
Typical torque-speed curve for a split-phase induction motor
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.6
Starting torque is low – 1.5 - 2 times running torque.
Starting current is 5 – 7 times the running current.
Torque reduces when start winding cuts out.
Auxiliary coil must be disconnected so number of starts per hour are limited.
Reversing swap polarity on any winding
Typical size 1kW or less
Application Grinders, Sanders, small lathes & drilling machines. (note how drilling machine can be held without turning at start).
Go to workshop and test split phase motors. Use skill practice 1
Students can do tutorial 5 at this point.

## Slide 12: Protection
<number>
Motor protection and isolation requirements are specified by AS/NZS 3000:2007 in section 4.13.
Unattended split-phase motors rated higher than 240 VA are required to have protection against over-temperature.
Protection devices include a thermistor embedded in the winding and a bimetal snap-action switch.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 13: Testing and fault-finding
<number>
Common faults in a single-phase induction motor are dust and dirt build-up inside the motor, and bearing failure.
If a motor won’t start, check for faulty centrifugal switch contacts, operation of the thermal overload, an open circuit auxiliary or main winding, a locked rotor or loss of supply.
If the motor hums and attempts to start, the load may be jammed.
Notes: 31 Jul 2026
Install HV equipment
<number>
Go to workshop

## Slide 14: Insulation resistance
<number>
Tests include measuring the DC resistance of both windings and measuring the insulation resistance between windings and motor frame, which should be earthed.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.7

## Slide 15: 23.2 Capacitor motors
<number>
Typical capacitor motors
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.8
Capacitor starts are provided to give more torque and smoother running
Three types Cap start Cap Start/Cap Run Permanently Split capacitor
Typical sizes range 30w over 10kW

## Slide 16: Motor capacitors
<number>
Motor capacitors range from a few microfarads to over 200 µF. They have an AC voltage rating.
Capacitors in the starting circuit are often non-polarised electrolytics.
Capacitors in circuit while the motor is running are usually oil-filled paper or plastic film dielectric types.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.9
Capacitors have number of starts per hour on them, rated to specific voltages and farads.
Must be replaced with suitable capacitor.
Show Caps start motor from motor room
Next slide to introduce Cap start and demo torque

## Slide 17
<number>
Capacitor start motor
Circuit of a capacitor start, induction run motor in which the phase difference between the start and run currents approaches 90º
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.10
Explain operation with Capacitor giving phase shift leading (its not 90 degrees from Voltage supply as its in series with start coil).
Overall phase shift is 90
Capacitor duty times can vary from 5-10 seconds which means motor must get to 75% of speed before then to allow cap to get disconnected from circuit.
Next slide to discuss torque

## Slide 18
<number>
Current relay in the start circuit
(a) A current relay is used in the start circuit of capacitor motors rated above 750 W
(b) Capacitor start motors have a starting torque up to four times the rated torque
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.11
On motors above 750W current relay is used
4 x torque by using capacitor,
Very common motor, can be reversed when running
Air con & refrigeration

## Slide 19
<number>
Capacitor start, capacitor run motor
The auxiliary (start) winding is always connected to the supply via either of the two capacitors.
The start capacitor has a greater capacitance than the run capacitor
This type of motor has a good starting torque and smooth running
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.12
Keeping capaicitor in the circuit gives a more uniform magnetic field due to 90 degree phase shift, therefore its a quieter motor.
Run cap also increases the motors breakdown torque, improving its efficiency and power factor.
Start cap about 10-15 times the value of run cap
Main use compressors (& air con) unique to floor polishers

## Slide 20: Permanently-split capacitor motor
<number>
A permanently-split capacitor motor does not have a starting switch.
It is reversed by adding an external switch that selects which of the identical windings has a capacitor in series with it.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.13
Two identical windings
Cap in series with one of them
Reverse by using switch to change capsitor winding configuration. (redraw on board)
Due to only one capacitor its torque is reduced but it remains quiet and smooth, its main task is ceiling fans.

## Slide 21: Faults in capacitor motors
<number>
As well as the faults that can occur in any induction motor, a capacitor motor can fail due to a faulty capacitor.
Capacitor faults are either an open-circuit, low resistance dielectric which means it can’t hold a charge, or a short-circuit.
A failing capacitor can also become leaky in that its dielectric seeps outside the can.
Notes: 31 Jul 2026
Install HV equipment
<number>
Tutorial 6 page 34

## Slide 22: 23.3 Shaded-pole induction motors
<number>
Shaded-pole motors are used in all kinds of fans, small pumps, clothes driers and have power ratings that rarely exceed a few hundred watts
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.14
Pass out Shaded pole induction motors
Explain it gets its name from the closed copper loop around the magnetic poles.
Small machines no greater than a few hundred watts.
Small fans pumps etc. Low torque.

## Slide 23: Shaded-pole operation
<number>
The shading rings in a shaded-pole motor cause the flux to concentrate in different parts of the poles, depending on how fast the current is changing
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.15
Coil has low resistance, large current, instantaneous strong magnetic field
Step through how magnetic field is concentrated to one side as current rises rapidly.
Lenz's law causes opposing field in shaded pole.
High slip speed,
Very simple robust construction
Not normally reversible unless two set of shading rings are fitted.
Very inefficient, loose laminations, sticking motor,, generally not worth repairing

## Slide 24: 23.4 Universal motors
<number>
The universal motor is not an induction motor, as it has a wound armature like those in a DC motor.
They are called universal because they operate from AC and DC.
The universal motor is used in mains-powered hand tools (drills, saws, planers, etc.), vacuum cleaners and applications where a high speed, relatively small motor is required.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 25: Example universal motor
<number>
The field coils are in series with the armature, and the stator and armature core are laminated
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.16
NOT INDUCTION
Wound armature in series with stator coils. Magnetic feild is produced by current into the armature & stator.
Operates on AC & DC draw circuit to show current direction on AC and DC. Demo with motor
Very high speed 20000RPM Unloaded, can cause machine to damage its armature Show you tube clip
small machine

## Slide 26: Circuit and torque-speed curve
<number>
Maximum torque of a universal motor is produced at start-up, and reduces significantly with speed.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 23.17
Draw circuit two represent reversal
Operation is,
as current is limited by coil & rotor resistance then it is quite high at start.
Therefore high torque
As motor turns Back EMF reduces the current in the circuit. The faster the armature the less current.
VT = (IZ)+Vg I = VT-Vg/Z
Power under 1kW, but good size ratio for power.
Poor efficiency prone to faults, sparking brushes, commutator can wear windings burn out
Sparking causes radio interference.

## Slide 27: Chapter summary
<number>
All single-phase induction motors require some means of creating a rotating magnetic field to start the rotor turning.
Once rotating above a certain speed, the rotor and stator magnetic fields produce the rotational torque.
All induction motors have a squirrel cage laminated steel rotor. The cage is usually made of aluminium.
Notes: 31 Jul 2026
Install HV equipment
<number>
Do Skill practical 3 in book on DC betts.
Do skill practical of series universal on 230 volt motors.
Do Philips tutorial questions
Do learning resource tutorial 7

## Slide 28: Chapter summary (2)
<number>
A split-phase induction motor has two windings, one with a higher resistance and lower inductance (auxiliary winding) than the other (main winding).
This creates a phase shift between the winding currents, giving a rotating field that can start the motor turning.
The auxiliary winding is disconnected from the supply when the motor reaches around 75 per cent of its rated speed.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 29: Chapter summary (3)
<number>
The auxiliary winding is disconnected from the supply by a centrifugal switch mechanism, or a current relay in series with the main winding.
A capacitor start motor has a large value capacitor in series with the auxiliary winding that provides additional phase shift between the winding currents during starting, giving the motor an increased starting torque.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 30: Chapter summary (4)
<number>
A permanently-split capacitor motor has two identical windings with a capacitor permanently in series with one of them.
It does not have a start switch, it is easily reversed and runs smoothly and quietly.
A shaded-pole motor has a copper shading coil fitted to the trailing tips of the stator poles.
It has limited starting torque, low efficiency, and cannot be easily reversed.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 31: Chapter summary (5)
<number>
A universal motor runs on AC and DC, and has a wound armature in series with the field coils.
The highest torque occurs at start-up, it can reach high speeds when unloaded, and features a high power to weight ratio.
Tests on a motor to prove serviceability include winding resistance tests, confirming correct operation of the start switch mechanism or relay, and measuring the insulation resistance between windings and motor frame.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 32: Equation summary
<number>
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 33: Equation summary (2)
<number>
where:
s% = percentage slip
ns = synchronous speed
n = rotor speed
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 34: Equation summary (3)
<number>
where:
fr = rotor frequency
f = supply frequency
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 35: Equation summary (4)
<number>
where:
Pin = VI cos ϕ
Notes: 31 Jul 2026
Install HV equipment
<number>