## Slide 1
Lesson 6
Chapter 21
Transformers
Sections
21.8 Transformers in parallel
21.9 High voltage safety

## Slide 2: 21.8 Transformers in parallel
Transformers in parallel should have the same:
percentage impedance (or regulation)
voltage ratio
instantaneous polarity of the secondary voltages
phase sequence (three-phase only)
phase difference between primary and secondary terminals (three-phase only).

## Slide 3: Percentage impedance (or regulation)
Notes: Figure 21.34

## Slide 4: Voltage ratio
When transformers are connected in parallel, their turns (voltage) ratio must be the same.
If not, the transformer with the higher output voltage will cause a current to flow in the other transformer, called a circulating current.
It is not unusual for a small value of circulating current to flow, which is acceptable if the transformers are not fully loaded.

## Slide 5: Polarity
If two voltages have the same polarity and the same value, there is no potential difference between them as in (a); otherwise the potential difference is twice the individual voltages as in (b)
Notes: Figure 21.35

## Slide 6: Determining polarity
Test set-up to determine the polarity of a transformer
Notes: Figure 21.36

## Slide 7: Three-phase transformers in parallel
Test set-up when connecting two three-phase transformers in parallel. Winding C has reversed polarity, indicated by the
460 V voltmeter reading.
Notes: Figure 21.37

## Slide 8: Phase sequence
Phase sequence only applies to polyphase transformers.
Phase sequence refers to the order in which each phase reaches its maximum voltage, which can be A-B-C or
A-C-B.
The order of phase sequence is not important, simply that both transformers must have the same phase sequence.

## Slide 9: Inherent phase angle
Transformers that belong to the same vector group can be connected in parallel, all other requirements having been met.
Transformers belonging to different vector groups cannot be operated in parallel without altering the internal connections of one of them.

## Slide 10: 21.9 High voltage safety
When working on high voltage equipment, an access permit is required, the equipment is isolated, danger tagged, and various points of the equipment are earthed
Notes: Figure 21.38

## Slide 11: Summing up
Transformer winding terminals are marked with letters and subscript numbers in accordance with AS 60076.1 to identify the start and end of each winding.
Three-phase transformer windings are generally connected in either delta or star configurations. Others include zigzag and open-delta.

## Slide 12: Summing up (2)
The vector group of a transformer identifies the phase difference between the primary and secondary voltages, which is typically 0º (group 1), 180º (group 2), –30º (group 3) or +30º (group 4).
Some transformers have a delta-connected tertiary winding to provide a path for 3rd order harmonics.

## Slide 13: Summing up (3)
Single-phase transformers being connected in parallel must have the same percentage impedance (or regulation), voltage ratio and polarity.
Three-phase transformers being connected in parallel must have all of the above plus the same phase sequence and inherent phase angle between primary and secondary terminals.