## Slide 2
Chapter 24
Synchronous machines
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 3: About this chapter
<number>
Synchronous machines run at a speed that locks to a frequency, typically 50 Hz. Synchronous motors come in various sizes, from a few watts to many megawatts.
Alternators are also synchronous machines and if driven by a prime mover provide most of our electricity supply.
This chapter:
Describes these machines and their operating principles
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 4: Contents
<number>
24.1 Alternators
23.2 Synchronous motors
23.3 Other types of synchronous motors
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 5: 24.1 Alternators
<number>
An alternator is an AC machine that when coupled to a prime mover, generates an alternating voltage. They come in a wide range of power ratings and output voltages
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.1
Ac machine driven by a prime mover, hydro, Steam or diesel, petrol engine and produces single & 3phase power.
Ratings 1KVA car alternator to 500MVA

## Slide 6: Automotive alternators
<number>
Automotive alternators are typically rated at less than 1 kVA, are usually three-phase and have diodes to convert the AC output to DC in order to charge the vehicle battery.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.2

## Slide 7: Basic alternator
<number>
An alternator has three main components: a magnetic field and a coil, in which one of them rotates relative to the other, and a set of slip rings.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.3
More coils and improved pole design will produce a good sinewave.
Discuss briefly basic principles.
Mention slip rings and brushes

## Slide 8: Three-phase alternator
<number>
A three-phase alternator with an armature rotating in a magnetic field created by a DC excitation current
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.4
Magnetic field on stator & armature is rotated by prime mover and has voltage induced into it.
This voltage and current is then drawn from the armature via sliprings and brushes.
Mention DC excitation as this keeps magnetic field constant and controls output
Only suitable for small motors

## Slide 9: Rotating field alternator
<number>
Two-pole rotating field three-phase alternator which produces three voltages with a phase difference of 120º
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.5
For larger machines it is better to rotate the magnet and apply DC via commutation.
Draw power direct from armature windings on the stator
Stator Laminated and rotor solid steel.
Next slide

## Slide 10: Salient pole rotor
<number>
Four-pole rotating field three-phase alternator and an example of a salient pole rotor
Notes: 31 Jul 2026
Install HV equipment
<number>
4 pole runs slow to produce 50Hz = 1500 rpm
2 pole high speed for 50 Hz 3000rpm
Salient pole gives an uneven air gap and helps produce better sine wave.

## Slide 11: Frequency and number of poles
<number>
For an alternator, the relationship between frequency, rotational speed and number of poles is found with the usual equation:
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 12: Speed and number of poles
<number>
Australia and New Zealand have a power frequency of 50 Hz, requiring alternators to run at a speed that produces this frequency.
The more poles, the slower the rotational speed to produce 50 Hz.
The number of poles required for a given rotational speed and frequency is:
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 13: Excitation
<number>
The field current for an alternator can be supplied by a DC shunt generator coupled to the shaft of the alternator
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 25.8
Dc excitation can be provided by DC shunt generator
Rheostat controls the field current & therefore the excitation, therefore the AC output.

## Slide 14: Circuit diagram
<number>
Circuit diagram of a shunt wound exciter supplying excitation current to a three-phase alternator
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.9
Explain the principles of operation

## Slide 15: Brushless excitation
<number>
Circuit diagram of a brushless excitation system, in which diodes convert the output of a 3-phase rotating armature alternator to provide excitation current for the main alternator
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.10
Explain that the Generator – Alternator - Prime mover
Solid state bridge rectifier feeds DC into rotor & Rheostat controls current into exciter windings
Benefits are no slip rings required.

## Slide 16: Alternator output voltage
<number>
where:
= alternator phase voltage
N = number of armature turns per phase
f = frequency of the generated voltage (Hz)
 = magnetic flux per pole in webers
k = machine constant
Notes: 31 Jul 2026
Install HV equipment
<number>
Example 24.1

## Slide 17: Open-circuit characteristics
<number>
Equivalent circuit of a single-phase alternator. Under no-load conditions, VT = EG
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.11
If generator is running with full excitation, but to load the Eg = Vt
Because no current is drawn no volt drop within the Alternator

## Slide 18
<number>
Open-circuit characteristics (2)
Open-circuit characteristic curve of an alternator, in which the field current is increased while the open-circuit voltage is measured
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.12
Shows the increase in excitation current which provides terminal voltage at rated speed
VT directly proportional to IF until saturation.

## Slide 19
<number>
Alternator rating
An alternator is rated by its:
terminal voltage at full load current
apparent power capability (VA rating)
frequency, which determines its rotational speed
number of phases
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 20
<number>
Alternator rating (2)
Equations to find the apparent power rating of an alternator are:
S = VI (single-phase alternator)
S = √3VLIL (three-phase alternator)
Notes: 31 Jul 2026
Install HV equipment
<number>
Do Example 24.2

## Slide 21
<number>
Loaded characteristics
Loaded alternator characteristic curves, in which the terminal voltage is measured while the load current is increased
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.13

## Slide 22: Phasor diagrams
<number>
Phasor diagrams of an alternator for loads taking the same current, at the same terminal voltage, but at different power factors
Notes: 31 Jul 2026
Install HV equipment
<number>
Step through book description

## Slide 23: Voltage regulation
<number>
where:
= no-load voltage
= full-load voltage
The terminal voltage of an alternator is rated at its full-load value.
The regulation of an alternator is the percentage change in terminal voltage when its full rated load is removed:
Notes: 31 Jul 2026
Install HV equipment
<number>
Do Example 24.3

## Slide 24: Voltage regulation curves
<number>
Curves showing the change in alternator terminal voltage when loads of different power factors are removed
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.15
Depending on load the terminal voltage will react differently.
On Resistive it drops slightly
On Capacitive it increases
On Inductive it drops dramatically

## Slide 25: Efficiency
<number>
The efficiency of an alternator is the ratio of the true power output (Pout) and the true power input (Pin):
Notes: 31 Jul 2026
Install HV equipment
<number>
Do example 24.4
Do practical

## Slide 26: Alternators in parallel
<number>
For a three-phase alternator to be connected in parallel with another three-phase power source:
Their voltages and wave-shapes should be the same, or close to.
The frequencies must be identical, which means the alternator being connected must be rotating at synchronous speed.
Both voltages must have the same phase sequence, and be in phase with each other
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 27: Synchronising an alternator
<number>
A synchroscope indicates the difference in frequency and phase relationship between two three-phase supply systems
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.16

## Slide 28: Three lamps dark method
<number>
If all lamps glow and darken together, the phase sequence is the same. The rate at which the lamps glow and darken indicates the difference in the frequencies of the alternator and the system.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.17

## Slide 29: Two bright, one lamp dark method
<number>
If L1 is dark and L2 and L3 are glowing, the alternator and the system are synchronised
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.18

## Slide 30: Summing up
<number>
Most alternators have a rotating field in the form of a rotor with field windings.
The windings in which the generated EMF is induced are in the form of coils wound in the stator. This winding is called the armature winding.
Alternators are designed to produce a sinusoidal voltage waveform at a rated voltage and frequency. They can be single-phase or multi-phase.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 31: Summing up (2)
<number>
The magnetic field in an alternator is produced by passing a DC excitation current through the rotor windings.
The terminal voltage of an alternator is set by the value of the excitation current.
The DC excitation source can be supplied to the rotor slip rings from a DC generator coupled to the alternator shaft.
A brushless exciter has an alternator and a three-phase rectifier built onto the shaft. This removes the need for slip rings.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 32: Summing up (3)
<number>
Alternators are rated by their full-load voltage.
The excitation current is set to achieve the correct voltage for each type of load.
When a load is removed, the terminal voltage either rises or falls, depending on the type of load.
If the load is resistive (unity power factor) or inductive (lagging power factor), the terminal voltage will rise. It will rise more for an inductive load than a resistive load.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 33: Summing up (4)
<number>
When a capacitive load is disconnected, the terminal voltage of the alternator falls.
An alternator can be connected in parallel with another alternator or power bus bars only when both are in synchronism in terms of frequency and phase difference.
When an alternator is in parallel with another power source, it will run at the synchronous speed set by the power source, either as a motor or as a generator. It will run as an alternator when its prime mover provides enough power.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 34: 24.2 Synchronous motors
<number>
An alternator can operate as a synchronous motor.
There are two main categories of synchronous motors:
those that need an excitation source
those with a magnetised rotor that do not need external excitation, called non-excited motors
These motors are generally rated at less than 1 kW, many types down to a only few watts.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 35: Example synchronous motors
<number>
The ship propulsion motor has a similar construction to an alternator, the smaller motors have a permanent magnet rotor
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.19

## Slide 36: Separately excited motor
<number>
Synchronous motor with a separate DC exciter
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.20

## Slide 37: Operating principle
<number>
When a three-phase supply is connected to the stator of a synchronous motor, a rotating field is set up in the stator that travels at synchronous speed.
Once the motor is running at its synchronous speed, it will remain at this speed regardless of load, unless the load increases to a point that causes the motor to loose synchronism.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 38: Starting methods
<number>
Methods of bringing a synchronous motor up to speed:
Exciter as a motor: when the motor is at synchronous speed, its field is connected to the exciter, which is now a generator and no longer a motor.
Pony motor: once the motor is up to speed, AC power and DC excitation is applied to the synchronous motor.
Variable frequency drive (VFD): by setting the frequency of the drive system to a very low value and gradually increasing it.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 39: Induction motor start
<number>
Many synchronous motors have rotors fitted with ‘damping bars’, also called ‘amortisseur windings’.
In this type of rotor, an assembly like the squirrel cage in an induction motor is built into the pole faces of the rotor.
Synchronous motors with damping bars in the rotor can be started as an induction motor.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 40: Damping bars
<number>
3 MW synchronous motor rotor with amortisseur winding (damping bars), and the rotor laminations
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.21

## Slide 41: Loading the motor
<number>
At no load, a synchronous motor rotor pole is central with the rotating stator field, when loaded, it lags the field by torque angle α. When overloaded, the magnetic coupling is lost and the motor stalls.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.22

## Slide 42: Phasor diagrams
<number>
Effect of load on the line current in a synchronous motor.
α is the torque angle, and ϕ is the phase difference between the motor voltage and current.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.23

## Slide 43: Varying the excitation current
<number>
Varying the excitation current varies the motor power factor.
Too little causes a lagging power factor.
Too much causes a leading power factor.
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.24

## Slide 44: V-curve
<number>
V-curves of a synchronous motor showing how power factor and motor current change with a change in field excitation current
Notes: 31 Jul 2026
Install HV equipment
<number>
Figure 24.25

## Slide 45: Hunting
<number>
When the load on a synchronous motor changes, the torque angle changes in a direction depending on whether the load has increased or decreased.
The change in torque angle has to occur against the inertia of the rotor, which means the rotor tends to swing around the point of equilibrium.
The average rotor speed remains constant, but with variations above and below synchronous speed. This effect is called hunting.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 46: Minimising hunting
<number>
Hunting can be reduced or prevented by increasing the excitation current to make the magnetic bond stronger.
Another technique is the use of damper bars fitted to the rotor.
The hunting effect induces a current in the bars, which by Lenz’s law will act to prevent the motion causing the induced current.
This dampens the swaying action of the rotor, and establishes smoother running.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 47: Reversing
<number>
A synchronous motor can be reversed by swapping any two phases supplying the stator.
This reverses the direction of the rotating field as in any three-phase motor.
If the motor is started with a pony motor or a DC exciter, its rotational direction will also have to be reversed.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 48: Stopping
<number>
A large synchronous motor has considerable inertia, and may take a while to stop rotating.
On method to stop the motor is dynamic braking, in which the motor becomes an alternator supplying current to either a short circuit or load resistors.
Another method is mechanical braking with brake shoes around the motor shaft.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 49: Efficiency
<number>
The losses in a synchronous motor are similar to those in an alternator.
These include rotational losses such as bearing friction, windage and brush friction at the rotor slip rings, I2R losses in the stator and exciter windings, iron losses and losses due to the exciter.
As for all machines, efficiency:
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 50: 24.3 Other types of synchronous motors
<number>
Other types of synchronous motors include:
Synchronous induction motor, which is similar in construction to the wound rotor induction motor.
Single-phase synchronous motors that include:
Reluctance motor
Hysteresis motor
Permanent magnet motor
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 51: Summary
<number>
A synchronous motor runs at a fixed speed determined by the frequency of the supply and the number of poles in the motor.
Motors above 1 kW are excited by an external DC supply, smaller motors are non-excited and do not need a separate DC supply.
A synchronous motor is not normally self-starting. Once brought up to speed, it will lock into the rotating stator field and maintain synchronous speed.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 52: Summary (2)
<number>
Amortisseur windings, also called damping bars, are fitted to the rotor of a synchronous motor to prevent it hunting, and to also provide a means of starting the motor.
In this case, the bars allow the motor to start as an induction motor.
When the load on a synchronous motor is increased, the rotor speed remains constant, but the rotor shifts backwards by an amount called the torque angle.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 53: Summary (3)
<number>
The power factor of a synchronous motor depends on the level of DC excitation.
An under-excited motor has a lagging power factor, an over-excited motor has a leading power factor.
The optimum exciting current gives the minimum stator current for that load at unity power factor.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 54: Summary (4)
<number>
Because power factor can be determined by excitation, synchronous motors are sometimes used to improve power factor.
In this application, the motor is a synchronous capacitor.
Small synchronous motors are non-excited and some types have a permanent magnet rotor.
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 55: Summary of equations
<number>
where:
ns = synchronous speed in RPM
f = supply frequency in hertz
p = number of poles
or
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 56: Summary of equations (2)
<number>
where:
= alternator phase voltage
N = number of armature turns per phase
f = frequency of the generated voltage (Hz)
 = magnetic flux per pole in webers
k = machine constant
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 57: Summary of equations (3)
<number>
Apparent power:
S = VI (single-phase alternator)
S = √3VLIL (three-phase alternator)
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 58: Summary of equations (4)
<number>
where:
= no-load voltage
= full-load voltage
Notes: 31 Jul 2026
Install HV equipment
<number>

## Slide 59: Summary of equations (5)
where:
Pin = Pout + losses
<number>
Notes: 31 Jul 2026
Install HV equipment
<number>