## Slide 1
Lesson 5
Chapter 21
Transformers
Transformers Test 1
Section
21.7 Transformer connection & harmonics

## Slide 3: 21.7 Transformer connections
Letters are assigned; the same letter is used for all windings on one limb of the core.
High voltage winding is identified with capital letters, low voltage winding on the same core is identified with a corresponding small letter.
An auxiliary (or third) winding is identified by a capital letter for that phase, preceded by the numeral 3 (e.g. 3A).
The start of a winding is identified by number 1 written as a subscript (A1 or a1), the end by number 2 as a subscript (A2 or a2).

## Slide 4: Winding identification
Transformer winding markings as specified by Australian Standard AS 60076.1 Power transformers
Notes: Figure 21.30

## Slide 5: Three-phase transformers
Three ways to connect each winding of a three-phase transformer are: star, delta and inter-star or zigzag. Star and delta are the most common.
The four ways of combining star and delta connections in a transformer are:
star primary and star secondary (star–star)
star primary and delta secondary (star–delta)
delta primary and delta secondary (delta–delta)
delta primary and star secondary (delta–star).

## Slide 6: Connections and symbols
Star–star and delta–star transformer connections and symbols
Notes: Figure 21.31

## Slide 7: Phase shift
Star–delta connections have a phase difference between the primary and secondary voltages. Star–star and delta–delta have no phase shift:
star–star – 0º phase shift
star–delta – 30º phase shift, V2 leading V1
delta–delta – 0º phase shift
delta–star – 30º phase shift, V2 lagging V1.

## Slide 8: Vector group
A vector group is a standard way of identifying transformer winding connections and phase shift.
The code has two or three letters, followed by one or two digits. Capital letters are for the high voltage windings and small letters for the low voltage:
Y or y – star connection
D or d – delta connection
N or n – neutral point is brought out.

## Slide 9: Typical vector groups
Phase shift is shown with a clock face.
1 o’clock is 30º lagging, 11 o’clock is 30º leading.
Notes: Figure 21.32

## Slide 10: Name plate – vector group
Nameplate from a 60 MVA 132 kV/33 kV star–star power transformer with a delta-connected 11 kV tertiary winding
Notes: Figure 21.33

## Slide 11: Tertiary winding and harmonics
The B–H curve of a transformer core is not linear, which means its magnetising current contains harmonics, in particular third-order harmonics (150 Hz).
The harmonic component of the magnetising current flows through the neutral of a star-connected winding, or around any delta-connected winding.
Some transformers have a third winding connected in delta, called a tertiary or stabilising winding to provide a path for third-order harmonics.