## Slide 1
Lesson 2
Chapter 21
Transformers
Section
21.4 Transformer operation

## Slide 2: 21.4 Transformer operation
Equivalent circuit of a single-phase transformer on no-load
Notes: Figure 21.16

## Slide 3: Transformer on no-load
A transformer’s no-load current consists of the core loss current Ic and the magnetising current Im
Ic is a loss (generates heat) and is in phase with the primary voltage (V1)
Im lags the primary voltage by 90º.
Phasor diagram for a transformer on no-load
Notes: Figure 21.17

## Slide 4: Transformer on load
Equivalent circuit of a single-phase transformer on load
Notes: Figure 21.18

## Slide 5: Transformer with a resistive load
Secondary current I2 is in phase with the secondary terminal voltage.
I2' is the secondary reflected current in the primary winding.
The phasor addition of Io and I2' gives the total primary current I1.
The angle between I1 and V1 gives the power factor.
Phasor diagram for a transformer on load
Notes: Figure 21.19

## Slide 6: Transformer with an inductive load
Secondary current I2 lags the secondary terminal voltage.
I2' is the secondary reflected current in the primary winding.
The phasor addition of Io and I2' gives the total primary current I1.
The angle between I1 and V1 gives the power factor.
Phasor diagram for a transformer with inductive load
Notes: Figure 21.20

## Slide 7: Summing up
In a practical transformer:
no-load current is the phasor sum of the magnetising current and the core loss current
primary current of a loaded transformer is the phasor sum of the no-load current and the current reflected in the primary by the secondary current
the power factor of an unloaded transformer is usually very low, loading a transformer improves the power factor.