- 2 Types of Emergency Lighting: Maintained vs. Non-maintained

Do you remember your school fire drills? What about your yearly occupational safety and hazard employee training? Have you ever had to exit a building because of a valid emergency? A fire? A gas leak? A power outage? Another kind of threat? Was there panic? Were you in a familiar place where you knew what to do and where to go? Was it somewhere unfamiliar?

You probably took note of your entry and exit routes as well as subconsciously observing the exit signs. Whether you are aware of it or not, emergency lighting is also there to guide you to safety in the event of an emergency.

Emergency lighting is divided into two main categories.

- Maintained Emergency Lighting

When emergency lights are on all the time, they are known as maintained emergency lighting. Maintained lighting is often found where large numbers of individuals congregate. Preventing complete darkness, maintained lighting is designed to continue to work even when there is a power outage. Maintained lighting is occasionally used as standard lighting as well. You may be subconsciously aware of maintained emergency lighting in movie theaters, auditoriums, shopping malls, hospitals, airplanes, and windowless offices and classrooms.

- Non-maintained Emergency Lighting

If maintained lighting is on 24/7, then non-maintained lighting is definitely not on all of the time. In fact, non-maintained lighting is only engaged when there has been a power outage. Often battery-operated, non-maintained lighting regularly charges itself through its own power supply to ensure that it will activate when the power has gone out.

Exit signs, though different from emergency lighting may also be used as emergency lights, and therefore should be maintained or non-maintained depending on the building needs. They serve a double function of providing light and direction for escape routes from the building.

Both maintained and non-maintained emergency lighting require regular testing to ensure the safety of the building occupants in the event of an emergency. According to regulations, emergency lighting should illuminate the building for a minimum of one-hour to assist evacuees. Reentry and reoccupation of the building may require these lights to stay on longer.

The type of emergency lighting system needed is determined by the type and layout of the building, the type of business, and the kind of occupancy.

Contact the experts with Pye Barker Fire Safety to install or test your emergency lighting today.

An emergency power system is an independent source of electrical power that supports important electrical systems on loss of normal power supply. A standby power system may include a standby generator, batteries and other apparatus. Emergency power systems are installed to protect life and property from the consequences of loss of primary electric power supply. It is a form of a continual power system.

They find uses in a wide variety of settings from homes to hospitals, scientific laboratories, data centers,[1] telecommunication[2] equipment and ships

The key parameters for emergency lighting as defined in NFPA 101 are the requirements for stairs to have a minimum of 10 fc (108 lux) measured at the walking surface, and a minimum of 1.0 fc (10.8 lux) for floors and walking surfaces with an exception for assembly occupancies of 0.2 fc (2.2 lux) during periods of performances or projections involving directed light (a movie theater).

In the event of a power outage, the emergency lighting must be transferred to its alternate source within 10 sec. Additionally, battery-powered emergency lighting shall be continuously available for 1.5 hours after the power outage. The emergency illumination shall be spaced to provide initial illumination along the defined path of egress of not less than an average of 1.0 fc (10.8 lux) and not less than 0.1 fc (1.1 lux) at the floor of the defined pathway. At the end of 1.5 hours, the illumination levels are permitted to decline along the path of egress as the emergency power source discharges to an average of 0.6 fc (6.5 lux) but not less than 0.06 fc (0.65 lux). In order to provide sufficient contrast and subsequent visual acuity, the maximum to minimum illumination uniformity ratio shall be no greater than 40:1.

Interestingly, the IBC 2012 is somewhat contrary to NFPA 101, stipulating in IBC 1006.2 the following: “The means of egress illumination shall not be less than 1 fc (11 lux) at the walking surface.” Note that this stipulation does not say “average” nor does it imply an average number; it is clearly the minimum requirement for emergency egress lighting, and is required by some AHJs. The exception to this applies to certain assembly occupancies. Fortunately, the performance of the emergency lighting system is the same in both the IBC and NFPA 101. Ultimately, the challenge presented is getting the AHJ to accede to the NFPA 101 requirements in lieu of IBC 1006.2, which certainly offers more specific parameters than can readily be achieved.

LOCATION OF EMERGENCY LIGHT

EXIT SIGN MOUNTING