1. The maximum current rating of a circuit breaker to protect a mixed circuit using both2.5 & 1.5 mm2 cables is : _______________ AS/NZS 3000 reference __________

25A

C5 NUMBER OF POINTS CONNECTED TO CIRCUITS

C5.1 Number of circuits

Each item of equipment that has a current rating in excess of 20 A per

phase should be connected to a separate and distinct circuit

2. Is an RCD required to protect this circuit if it is connected in a domestic installation?

____________________________________ AS/NZS 3000 reference __________

Yes

2.6.1 General

The use of fixed setting RCDs with a rated operating residual current not

exceeding 30 mA is recognized as providing additional protection in areas

where excessive earth leakage current in the event of failure of other

measures of protection or carelessness by users could present a significant

risk of electric shock.

2.6.2.4 Arrangement

Where additional protection of final subcircuits is required, in accordance

with Clause 2.6.3, the final subcircuits shall be arranged as follows:

(a) In all electrical installations where—

(i) the number of RCDs installed exceeds one; and

(ii) more than one lighting circuit is installed,

lighting circuits shall be distributed between RCDs.

(b) In residential installations—

(i) not more than three final subcircuits shall be protected by any

one RCD; and

(ii) where there is more than one final subcircuit,

a minimum of two RCDs shall be installed.

NOTE: These arrangements are intended to minimize the impact of the

operation of a single RCD.

2.6.3.2.2 Domestic and residential installations—Australia only

Additional protection by RCDs with a maximum rated residual current of

30 mA shall be provided for all final subcircuits in domestic and residential

electrical installations.

Where protection of final subcircuits is required, RCDs shall be installed at

the switchboard at which the final subcircuit originates.

These installations include but are not limited to—

(a) individual domestic electrical installations;

(b) residential areas of electrical installations;

(c) multiple residential electrical installations that are provided for

common use; or

(d) external lighting installations in common areas of multiple residential

electrical installations.

2.6.3.2.3.3 Requirements for additional protection

Additional protection by RCDs with a maximum rated residual current of

30 mA shall be provided for final subcircuits with a rating not exceeding

32 A supplying—

(a) socket-outlets;

(b) lighting;

3. State the minimum rating in amps of an RCD that could be used to protect this

circuit.

____________________________________ AS/NZS 3000 reference __________

30 mA

2.6.1 General

The use of fixed setting RCDs with a rated operating residual current not

exceeding 30 mA is recognized as providing additional protection in areas

where excessive earth leakage current in the event of failure of other

measures of protection or carelessness by users could present a significant

risk of electric shock.

4. Where 2 or more socket outlet circuits are installed in a dwelling, AS/NZS 3000

uses a diverse approach when calculating the maximum demand each point will

contribute to a loading of a circuit. Using this approach, determine the loading for

the following circuit if it is installed using flat TPS twin and earth cable completely

surrounded in thermal insulation:

• 4 double power points and 10 light points

_______________________________________________________________

_______________________________________________________________

_________________________________ AS/NZS 3000 reference __________

• Cable size or sizes for the above circuit

_________________________________AS/NZS 3000 reference __________

• Circuit breaker used for protection ______AS/NZS 3000 reference __________

Refer

Cable size

Circuit Breaker

5. What is the minimum separation between a circuit cable supplying light points and a

telephone cable when installed in a ceiling space?

_______________________________ AS/NZS 3000 reference __________

50mm2

3.9.8.4 Proximity to non-electrical services

(c) Telecommunication services Requirements for the separation of

telecommunications cables from low voltage and high voltage systems

are provided—

(i) for Australia, in AS/CA S009; and

(ii) for New Zealand in the NZ Telecommunications Forum (TCF)

Premises Wiring Guidelines.

Separation from telecommunications services shall be as shown in

Figures 3.8 and 3.9.

NOTE: The documents listed in Item (c) contain distances and other

measures for the separation of telecommunications cables from low voltage

cables as follows:

(a) On surfaces or concealed in walls, floors or ceilings, such as depicted in

Figure 3.8.

(b) Cables in common ducting.

(c) In underground trenches, such as depicted in Figure 3.9.

(d) Under-carpet wiring.

(e) Aerial cables.

6. List 3 methods that are deemed to permanently separate communication

cables from any LV power cable

i) _______________________________________________________

ii) _______________________________________________________

iii) _______________________________________________________

(c) Telecommunication services Requirements for the separation of

telecommunications cables from low voltage and high voltage systems

are provided—

(i) for Australia, in AS/CA S009; and

(ii) for New Zealand in the NZ Telecommunications Forum (TCF)

Premises Wiring Guidelines.

Separation from telecommunications services shall be as shown in

Figures 3.8 and 3.9.

(1)Barrier of durable insulating material or metal

OR

(2)50 mm minimum separation

(3) Conduit

7. Which Australian standard sets the installation requirements for

telecommunication cabling?

______________________________________________________________

Telecommunication services Requirements for the separation of

telecommunications cables from low voltage and high voltage systems

are provided—

(i) for Australia, in AS/CA S009; and

(ii) for New Zealand in the NZ Telecommunications Forum (TCF)

Premises Wiring Guidelines.

8. Define the following:

Extra low voltage

________________________________ AS/NZS 3000 reference __________

Low Voltage:

________________________________ AS/NZS 3000 reference __________

1.4.128 Voltage

Differences of potential normally existing between conductors or

between conductors and earth as follows:

(a) Extra-low voltage Not exceeding 50 V a.c. or 120 V ripple-free

d.c.

(b) Low voltage Exceeding extra-low voltage, but not exceeding

1000 V a.c. or 1500 V d.c.

(c) High voltage Exceeding low voltage.

9. Is it permissible to install low voltage power cables and telecommunication

cables in the same section of a skirting duct?

______________________________________________________________

_____________________________ AS/NZS 3000 reference __________

3.9.8.4 Proximity to non-electrical services

Separation from telecommunications services shall be as shown in

Figures 3.8 and 3.9.

NOTE: The documents listed in Item (c) contain distances and other

measures for the separation of telecommunications cables from low voltage

cables as follows:

(a) On surfaces or concealed in walls, floors or ceilings, such as depicted in

Figure 3.8.

(b) Cables in common ducting.

(c) In underground trenches, such as depicted in Figure 3.9.

(d) Under-carpet wiring.

(e) Aerial cables

10.If an insulating shroud is required to be installed to provide segregation

between a telephone point and 230V Single phase power point installed

adjacent to each other, to which point should the shroud be fitted?

_____________________________ AS/NZS 3000 reference __________

3.9.8.4 Proximity to non-electrical services(c)