1. Refer to table 3.3 and state the minimum size cable permissible for :

Lighting circuits ___________________________________________

Socket Outlet circuits ________________________________________

2. Within what distance of the roof space access hole (manhole) is the wiring system

deemed likely to be disturbed?

__________________________________ AS/NZS 3000 reference ____________

within 50 mm from the face of

3.9.4.4 Protection methods

Where protection of a wiring system is required, in accordance with

Clauses 3.9.4.2 and 3.9.4.3.2, the wiring system shall be—

* (a) provided with adequate mechanical protection at a minimum of WSX3

to prevent damage (refer to Paragraph H5.4, Appendix H); or

3. Detail the method of fixing TPS cables within 1 metre of the access hole to avoid

mechanical damage.

__________________________________________________________________

__________________________________________________________________

__________________________________ AS/NZS 3000 reference ____________

Wiring systems that are fixed in position by fasteners, or held in position by

thermal insulation, or by passing through an opening in a structural

member, shall be protected by one of the methods outlined in

Clause 3.9.4.4 if they are concealed within 50 mm from the surface of a

wall, floor, ceiling or roof.

provided with adequate mechanical protection at a minimum of WSX3

to prevent damage (refer to Paragraph H5.4, Appendix H); or

4. What precautions are required for TPS cables installed in a hollow wall?

__________________________________________________________________

__________________________________________________________________

__________________________________ AS/NZS 3000 reference ____________

3.9.5 Wiring systems installed vertically

Where wiring systems are installed vertically, they shall be installed in

accordance with the requirements of Clauses 3.9.2 and 3.9.3 and in such a

manner as to avoid damage to any part of the wiring system that may be

caused by its own weight or method of support or fixing.

Adequate provision shall be made for the support of cables enclosed in a

wiring enclosure installed vertically. Cable supports shall be provided at

intervals not exceeding 8 m or as recommended by the cable manufacturer

5. Can black coloured insulation be used on the switch wire?

__________________________________ AS/NZS 3000 reference ____________

No 3.9.1 Table 4

6. State two colours that may be used to identify the neutral conductor.

__________________________________________________________________

__________________________________AS/NZS 3000 reference ____________

The maximum amount of insulation that can be removed when making a

connection is:

__________________________________________________________________

__________________________________ AS/NZS 3000 reference ____________

3.7.2.2 Preparation for connection

The insulation on a conductor shall not be removed any further than is

necessary to make the connection.

For connections between insulated conductors, the connection shall be

insulated to provide a degree of insulation not inferior to that of the

conductors. Any damaged insulation shall be reinstated.

8. Can stranded conductors be soldered to prevent spreading when terminating?

__________________________________ AS/NZS 3000 reference ___________

NO

3.7.2.5 Retention of stranded conductors

The ends of stranded conductors shall be secured by suitable means, so as

to prevent the spreading or escape of individual strands. They shall not be

soft-soldered before clamping under a screw or between metal surfaces

Active    Neutral

Earth

4.3.4 Socket-outlets in installation wiring

The installation wiring of the electrical installation shall terminate at a

suitable socket-outlet, the wiring to the electrical equipment being

continued by means of a plug and flexible cord or cable (see Figure 4.6).

10.For the following question, the maximum demand of each final sub-circuit is

assumed to be the current rating of the protective device for the circuit.

Determine the recommended number of 10A double socket outlets can be installed

on a 2.5mm2 flat TPS twin and earth cable, if it is protected by a 16A circuit breaker

in an air-conditioned office and the cable is installed partially surrounded in thermal

insulation.

C9