MIXED CIRCUIT CABLE SIZE AND CIRCUIT ARRANGEMENT

Lighting final sub-circuits that supply a combination of batten holders or luminaires,

together with small fixed appliances not exceeding _______ Watts such as exhaust

fans, heated towel rails, sweep fans etc, are actually mixed circuits. Due to the small

load demand and/or physical location of these appliances, they may be deemed as

lighting points and as such, these circuits are treated as dedicated lighting circuits

and not mixed circuits. It is typical in most domestic installations for these circuits to

be wired in 1.0mm2 or 1.5mm2 cables and protected by a circuit breaker up to 10A.

150 Watts

However, if a combination of lighting points and socket outlets are installed together

on a single circuit, an increase in cable size will most likely be required to meet the

demand of the circuit. In most circumstances socket outlets should only be

connected to conductors having a CSA of _______mm2 or greater (AS/NZS

3000:2007 – Table ________).

2.5 mm2

Typically, lighting points or appliances less than 150 W are wired off a 2.5mm2 socket

outlet circuit, using reduced 1.0mm2 or 1.5mm2 conductors. In some cases 2.5mm2

may be used for the entire circuit. NOTE: Where a mix of cable sizes are used on a

single circuit such as a mixed circuit, the circuit protection device must be installed to

protect the _____________ cable in the circuit.

each

2.5.1.3 Submains and final subcircuits—General arrangement

An overcurrent protective device or devices ensuring protection against

overload current and short-circuit current shall be placed at the origin of

every circuit and at each point where a reduction occurs in the currentcarrying

capacity of the conductors.

Refer to AS/NZS 3000:2007 clause 1.6.1 (b)

An electrical installation shall be designed to...... function _______________ as

intended.

1.6 DESIGN OF AN ELECTRICAL INSTALLATION

1.6.1 General

An electrical installation shall be designed to—

(a) protect persons, livestock and property from harmful effects;

(b) function correctly as intended;

(c) connect, operate safely and be compatible with the electricity

distribution system, or other source of supply, to which the

electrical installation is to be connected;

(d) facilitate safe operation, inspection, testing and maintenance; and

* (e) reduce inconvenience in the event of a fault.

For example, Table C5 in AS/NZS3000 gives the maximum rating for a circuit breaker to protect the 1mm2 cable partially surrounded in thermal insulation as ______ amps. This

circuit breaker rating would not satisfy the requirements of clause 1.6.1(b). When a 10 amp appliance is connected to the socket outlet and lights are switched on, the circuit would be overloaded and could trip the breaker.

The next size circuit breaker is ______ amps and would allow a 10A appliance and

many lights to operate at the same time without tripping. The minimum size cable would

then need to be increased to ______mm2. This would ensure correct operation of the

circuit to meet the requirements of the wiring rules.

For AS3000:2016 Table C6

10A

16A

1.5 mm2

Refer to AS/NZS 3000:2007 Table C8

This table may be used as a guide to the loading of points on a mixed circuit. Special

attention should be payed to notes c.g.h and i with reference to this table.

c) A double socket outlet is equal to ______ points.

g) This table only applies if 2 or more other socket outlet circuits are installed.

h) Socket outlets in mixed circuits must be wired in _______mm2 cable

i) Diversity has been used. A common sense approach needs to be adopted when

determining the intended use of the socket outlets on the circuit. Fixed equipment,

including that supplied via a socket outlet, should have its actual demand used

In AS3000:2016, it is table C7

For the purposes of determining the number of points, a multiple combination of

socket-outlets is regarded as the same number of points as the number of integral

socket-outlets in the combination

2

Socket outlets in mixed circuits must be wired in _______mm2 cable

See the rows without NP  -   2.5 mm2

2.5mm2

3. SEGREGATION OF CIRCUITS

By definition, to segregate means to ‘separate or isolate one thing from another’.

With respect to electricity, segregation is to:

• Separate one service from another; such as an electrical cable from a

telecommunications cable; or

• Provide separation of circuits of different ____________ levels; or

• To insulate or shield cables or wiring systems.

Voltage

3.9.8.2.2 Segregation

* Where conductors for different electrical installations, or for individual

occupancies forming part of single or multiple electrical installations are

installed in a common enclosure, they shall be effectively segregated from

each other within that enclosure.

3.9.8.3 Segregation of different voltage levels

Cables of high voltage circuits and cables of low or extra-low voltage

circuits shall not be enclosed in the same wiring system.

Cables of low voltage circuits and cables of extra-low voltage circuits shall

only be enclosed in the same wiring system where one of the following

arrangements is employed:

(a) The low voltage cables are of a type providing the equivalent of double

insulation.

(b) All cables or each conductor of a multi-core cable are insulated for the

highest voltage present.

(c) The low voltage cables are installed in a separate compartment of a

common cable trunking system having fixed and continuous barriers

between compartments.

Although wiring and wiring systems which are not installed with appropriate

segregation may have no apparent immediate consequence, the long term effects

of inadequately segregating systems and services, may lead to harmful effects of

persons, livestock or property in direct vilation of clause ___________ of

AS/NZS3000:2007.

3.9.8.4

AS/NZA3000:2016

3.9.8.4 Proximity to non-electrical services

(a) General The following conditions shall be satisfied when installing

electrical services:

(i) Wiring systems shall not be installed in the vicinity of services

that produce heat, smoke or fumes likely to be detrimental to the

wiring system.

Exception: Wiring systems may be installed in such locations

where the wiring system is protected from harmful effects by

shielding that does not affect the dissipation of heat from the

wiring system.

(ii) Where a wiring system is situated below services liable to cause

condensation (such as water, steam or gas services), precautions

shall be taken to protect the wiring system from harmful effects.

(iii) Where electrical services are installed close to non-electrical

services, they shall be so arranged that any reasonably

foreseeable routine operation carried out on the other services

will not cause damage to the electrical services.

NOTE: This may be achieved by suitable spacing between the services

or the use of mechanical or thermal shielding.

(iv) Wiring systems shall be suitably protected against the hazards

likely to arise from the presence of other services in normal use.

(v) Cables without sheathing or further enclosure shall not be

installed in enclosures where they are accessible to personal

contact or where they may contact other services, such as water,

gas, hydraulic or communications systems.

NOTE: Metal parts of other services may require bonding to the

earthing system in order to provide protection against earth faults, in

accordance with Clause 5.6.2.3.

Refer to clause - General:

Wiring systems shall be selected and installed in accordance with Clauses

__________ to __________ so as to avoid any _______________ effects arising

from the installation and use of the wiring systems in the following situations:

a) Between ___________ ____________ _______________.

b) Between different parts of the ________ electrical installation.

c) Between circuits of an electrical installation operating at different

___________, such as extra-low voltage and low voltage.

d) Between circuits of an electrical installation supplying different __________

services.

e) Between safety services and the remainder of the electrical installation.

NOTE: The regulations for safety services provide requirements for the

segregation of such wiring systems from other wiring systems.

f) Between electrical installations and ______ - _____________ installations,

such as _______ and _________ ___________.

g) Between electrical installations and __________________ and data cable

installations.

3.9.8.1 General

Wiring systems shall be selected and installed in accordance with

Clauses 3.9.8.2 to 3.9.8.4 so as to avoid any detrimental effects arising

from the installation and use of the wiring systems in the following

situations:

(a) Between different electrical installations.

(b) Between different parts of the same electrical installation.

(c) Between circuits of an electrical installation operating at different

voltages, such as extra-low voltage and low voltage.

(d) Between circuits of an electrical installation supplying different safety

services.

(e) Between safety services and the remainder of the electrical

installation.

NOTE: The regulations for safety services provide requirements for the

segregation of such wiring systems from other wiring systems.

(f) Between electrical installations and non-electrical installations, such

as gas and water supply.

(g) Between electrical installations and telecommunications and data

cable installations.

Refer to clause - Different electrical installations:

a) Conductors that form part of different electrical installations shall not be

installed within the one enclosure.

b) Where conductors of different domestic or non-domestic portions of an

electrical installation that form part of a multiple electrical installation terminate

in a common enclosure, they shall be effectively _______________ from each

other.

Exception: This requirement need not apply to switchboards at which such

circuits originate.

3.9.8.2 Different electrical installations

* 3.9.8.2.1 Common enclosure/cable

Conductors for the following applications shall not be installed within the

same pipe, tube, conduit or the same multi-core cable:

(a) Conductors that form part of different electrical installations.

or

* (b) Conductors that form part of individual occupancies of single or

multiple electrical installations.

Exception: These requirements need not apply to switchboards at

which circuits are terminated.

* NOTE: Wiring enclosures such as ducts or cable trays, with removable covers

or with no covers at all, where the cables can be accessed without cutting or

destroying the enclosure, are deemed to comply with this Clause (3.9.8.2.1).

NOTE: Effective segregation may be achieved by the use of independently

sheathed cables, barriers of fire-resisting material or by distance.

Refer to clause - Segregation of different voltage levels.

Cables of high voltage circuits and cables of low or extra-low voltage circuits shall

not be enclosed in the same wiring system.

3.9.8.3 Segregation of different voltage levels

Cables of high voltage circuits and cables of low or extra-low voltage

circuits shall not be enclosed in the same wiring system.

Cables of low voltage circuits and cables of extra-low voltage circuits shall

only be enclosed in the same wiring system where one of the following

arrangements is employed:

(a) The low voltage cables are of a type providing the equivalent of double

insulation.

(b) All cables or each conductor of a multi-core cable are insulated for the

highest voltage present.

(c) The low voltage cables are installed in a separate compartment of a

common cable trunking system having fixed and continuous barriers

between compartments.

Refer to AS/NZS 3000:2007 clause 1.4.98 – Voltage:

a) Extra-low voltage equals: __________________________________

b) Low Voltage equals: __________________________________

c) High Voltage equals: __________________________________

1.4.98 Voltage

Differences of potential normally existing between conductors or

between conductors and earth as follows:

(a) Extra-low voltage: Not exceeding 50 V a.c. or 120 V ripple-free d.c.

(b) Low voltage: Exceeding extra-low voltage, but not exceeding

1 000 V a.c. or 1 500 V d.c.

(c) High voltage: Exceeding low voltage.

AS/NZS 3000:2016

1.4.128 Voltage

Differences of potential normally existing between conductors or

between conductors and earth as follows:

(a) Extra-low voltage Not exceeding 50 V a.c. or 120 V ripple-free

d.c.

(b) Low voltage Exceeding extra-low voltage, but not exceeding

1000 V a.c. or 1500 V d.c.

(c) High voltage Exceeding low voltage.

Cables of low voltage circuits and cables of extra-low voltage circuits may be

enclosed in the same wiring system only where one of the following arrangements

is employed:

(a) The low voltage cables shall be of a type providing the equivalent of

____________ ______________.

(b) All cables or each conductor of a multi-core cable shall be insulated for the

____________ ____________present.

(c) The low voltage cables shall be installed in a _____________ compartment of

a common cable trunking system having fixed and continuous barriers

between compartments.

3.9.8 Prevention of mutual detrimental effects between services

3.9.8.1 General

Wiring systems shall be selected and installed in accordance with

Clauses 3.9.8.2 to 3.9.8.4 so as to avoid any detrimental effects arising

from the installation and use of the wiring systems in the following

situations:

(a) Between different electrical installations.

(b) Between different parts of the same electrical installation.

(c) Between circuits of an electrical installation operating at different

voltages, such as extra-low voltage and low voltage.

(d) Between circuits of an electrical installation supplying different safety

services.

(e) Between safety services and the remainder of the electrical

installation.

NOTE: The regulations for safety services provide requirements for the

segregation of such wiring systems from other wiring systems.

(f) Between electrical installations and non-electrical installations, such

as gas and water supply.

(g) Between electrical installations and telecommunications and data

cable installations.

3.9.8.3 Segregation of different voltage levels

Cables of high voltage circuits and cables of low or extra-low voltage

circuits shall not be enclosed in the same wiring system.

Cables of low voltage circuits and cables of extra-low voltage circuits shall

only be enclosed in the same wiring system where one of the following

arrangements is employed:

(a) The low voltage cables are of a type providing the equivalent of double

insulation.

(b) All cables or each conductor of a multi-core cable are insulated for the

highest voltage present.

(c) The low voltage cables are installed in a separate compartment of a

common cable trunking system having fixed and continuous barriers

between compartments.

Refer to clause - Proximity to non-electrical services.

When installing electrical services in proximity to non-electrical services such as

gas, water, telecommunications etc, the following conditions must be met:

• The wiring systems shall not be installed in the vicinity of services that

produce _________, _________ or __________ likely to be detrimental to

the wiring system.

• If the wiring system is situated below services liable to cause condensation

(such as water, steam or gas services), precautions shall be taken to protect

the wiring system from harmful effects.

• Electrical services installed close to non-electrical services shall be so

arranged that any reasonably foreseeable routine operation (such as

maintenance) carried out on the other services will not cause damage to the

electrical services.

• Cables without ___________ or further enclosure shall not be installed in

enclosures where they are accessible to ___________ ___________ or

where they may contact other services, such as water, gas, hydraulic or

communications systems.

• Wiring systems shall maintain a separation of not less than ______ mm from

any above-ground gas or water piping. Separation from underground gas

and water services shall be in accordance with Clause 3.11.5.

3.9.8.4 Proximity to non-electrical services

(a) General The following conditions shall be satisfied when installing

electrical services:

(i) Wiring systems shall not be installed in the vicinity of services

that produce heat, smoke or fumes likely to be detrimental to the

wiring system.

Exception: Wiring systems may be installed in such locations

where the wiring system is protected from harmful effects by

shielding that does not affect the dissipation of heat from the

wiring system.

(ii) Where a wiring system is situated below services liable to cause

condensation (such as water, steam or gas services), precautions

shall be taken to protect the wiring system from harmful effects.

(iii) Where electrical services are installed close to non-electrical

services, they shall be so arranged that any reasonably

foreseeable routine operation carried out on the other services

will not cause damage to the electrical services.

NOTE: This may be achieved by suitable spacing between the services

or the use of mechanical or thermal shielding.

(iv) Wiring systems shall be suitably protected against the hazards

likely to arise from the presence of other services in normal use.

WELCOME

(v) Cables without sheathing or further enclosure shall not be

installed in enclosures where they are accessible to personal

contact or where they may contact other services, such as water,

gas, hydraulic or communications systems.

NOTE: Metal parts of other services may require bonding to the

earthing system in order to provide protection against earth faults, in

accordance with Clause 5.6.2.3.

(b) Gas and water services Requirements for the separation of

distributed gas and water systems from low voltage wiring systems are

provided in the AS/NZS 5601 series for gas services and the

AS/NZS 3500 series for water services.

Wiring systems shall maintain a separation of not less than 25 mm

from any above-ground gas or water piping. Separation from

underground gas and water services shall be in accordance with

Clause 3.11.5.

AS3000:2016

Page 214

Loading: _______________________ AS/NZS 3000 reference _____________

Cable ratings: ___________________ AS/NZS 3000 reference _____________

Circuit breaker size:_______________AS/NZS 3000 reference _____________