# APPLICATIONS OF COGENERATION

Page 65

Cogeneration applications are usually classified with reference to the sector they appear:

- utility sector,

- industrial sector,

- building sector (called also residential-commercial-institutional sector),

- rural sector.

Cogeneration opportunities in each sector and related information are mentioned in the following.

## INDUSTRIAL COGENERATION

Many industrial processes require heat in order to be completed. They are classified according to the temperature level of the required heat:

- Low temperature processes (lower than 100C), e.g. drying of agricultural products, space heating or cooling, domestic hot water.

- Medium temperature processes (100-300C), e.g. processes in pulp and paper industry, textile industry, sugar factories, certain chemical industries, etc. In these processes heat is usually supplied in the form of steam.

- High temperature processes (300-700C), e.g. in certain chemical industries.

- Very high temperature processes (higher than 700C), e.g. in cement factories, primary metal industries, glass works.

## COGENERATION IN THE BUILDING SECTOR

Page 68

A combination of electrical and thermal load with level and duration appropriate for cogeneration often appears in buildings such as the following:

- houses and apartment buildings,

- hotels,

- hospitals,

- schools and universities,

- office buildings,

- stores, supermarkets, shopping centres,

- restaurants,

- swimming pools and leisure centres.

The list is not meant to be complete; in other buildings cogeneration may be feasible.

Cogenerated heat is used for domestic hot water, space heating or cooling, laundry facilities, dryers, swimming pool water heating. An indication of the electrical power required in various types of buildings is given in Table 1.

Table 1: Typical electrical load ranges in buildings.

| Building | Electric load (kW) |
| --- | --- |
| Restaurants Apartment buildings Supermarkets Hotels Hospitals Shopping centres Schools, universities Office buildings | 50 – 80 50 – 100 90 – 120 100 – 2000 300 – 1000 500 – 1500 500 – 1500 500 – 2000 |

## RURAL COGENERATION

Page 70

Cogeneration is not widespread in the rural sector, but its application can result in energy savings and economic benefits in rural communities. Promising rural applications of cogeneration include ethanol production, drying crops or wood, and heating greenhouses, animal shelters, or homes.

# IMPACTS OF COGENERATION

Page 72

Cogeneration can have both beneficial and adverse effects on the depletion of non-renewable energy (fuel) resources, on the utility system of a region or a country, on the environment, as well as on the society. Potential adverse effects could be mitigated substantially, if the cogeneration system is properly selected, designed, and sited, if it is carefully integrated in the energy system of the region, including existing and planned future energy supplies, and it is properly maintained and operated throughout its lifetime. A more detailed presentation of the effects follows.

## IMPACTS ON FUEL UTILIZATION

All cogeneration systems, if properly designed and operated, save fuel energy, because they have higher efficiency than the efficiency of separate production of electricity and heat (Error: Reference source not found, page Error: Reference source not found). For example, according to typical values of Error: Reference source not found, a steam-turbine cogeneration system reduces fuel energy consumption by about 15% with respect to the separate production of electricity by a steam power plant and of heat by a boiler; a Diesel engine system reduces fuel energy consumption by about 25% with respect to the separate production of electricity by a Diesel-engine generator and heat by a boiler. However, whether a cogeneration system saves an expensive, imported and non-renewable fuel such as oil, depends on the fuel used by the cogeneration system and the fuels used by the systems for the separate production of electricity and heat, which are displaced.

In addition to being more efficient than the separate production of electricity and heat, cogeneration systems save fuel energy for one more reason: usually they are much closer to the load than central power plants, thus reducing or even eliminating the losses of electrical energy along the transportation and distribution network, which can be as high as 8-10% of the electric energy at the source.

## IMPACTS ON ELECTRIC UTILITIES

In many places, utilities need to construct new power plants in order to either replace old ones or increase the capacity in view of an increase in demand. In these cases cogeneration can offer significant economic savings for utilities and it can be an attractive alternative to central power plants for the following reasons:

- Cogeneration adds new capacity and reduces the need for new investments in central power plants.

- The relatively small size of cogeneration systems and short construction lead-time can provide more flexibility than large base-load power plants for utilities in adjusting to unexpected changes in demand; furthermore cogeneration is a more cost-effective form of insurance against such changes than the overbuilding of central station capacity.

- Due to short construction lead-time, cogeneration can significantly reduce interest costs during construction, and consequently the overall cost of providing electricity.

- ENVIRONMENTAL IMPACTS

- Effects on Air, Water and Soil Quality

In addition to saving fuel and financial resources, cogeneration can also yield a reduction in polluting emissions, because it uses fuel more efficiently. The efficiency has a direct impact on emissions, as it is shown in Error: Reference source not found, provided the fuel used for cogeneration is not of lower quality than the fuel(s) used for the separate production of electricity and heat. In addition to the direct decrease in emissions, the reduced fuel consumption is accompanied by an indirect decrease in emissions in the rest of the fuel cycle: exploration, extraction, refining, processing, transportation, and storage.