## GAS TURBINE COGENERATION SYSTEMS

Page 19

Gas turbines either in a simple cycle or in a combined cycle (Chapter 1.1) are the most frequently used technology in recent cogeneration systems of medium to high power. Their electric power output ranges from a few hundred kilowatts to several hundred megawatts. On the other side of the spectrum, recent research and development aims at the construction of micro turbines, which have a power output of a few kilowatts.

Gas turbines have been developed as either heavy-duty units for industrial and utility applications, or as lightweight, compact and efficient aircraft engines. These engines are modified for stationery applications, in which case they are called “aeroderivative turbines”. In general, they are capable of faster start-ups and rapid response to changing load. Both gas turbine designs have been successfully used for cogeneration having as main advantages low initial cost, high availability, fast and low-cost maintenance, fuel-switching capabilities, high quality heat which can easily be recovered, and high efficiencies in larger sizes. In addition, the commercial availability of packaged units helped in their widespread applications.

### Gas Turbine Cycles

A gas turbine can operate either in open cycle or in a closed cycle.

#### Open-cycle gas turbine cogeneration systems

Most of the currently available gas turbine systems in any sector of applications operate on the open Brayton (also called Joule cycle when irreversibilities are ignored) (Error: Reference source not found): a compressor takes in air from the atmosphere and derives it at increased pressure to the combustor. The air temperature is also increased due to compression. Older and smaller units operate at a pressure ratio in the range of 15:1, while the newer and larger units operate at pressure ratios approaching 30:1.

The compressed air is delivered through a diffuser to a constant-pressure combustion chamber, where fuel is injected and burned. The diffuser reduces the air velocity to values acceptable in the combustor. There is a pressure drop across the combustor in the range of 1–2%. Combustion takes place with high excess air. The exhaust gases exit the combustor at high temperature and with oxygen concentrations of up to 15–16%. The highest temperature of the cycle appears at this point; the higher this temperature is, the higher the cycle efficiency is. The upper limit is placed by the temperature the materials of the gas turbine can withstand, as well as by the efficiency of the cooling blades; with the current technology it is about 1300C.

The high pressure and temperature exhaust gases enter the gas turbine producing mechanical work to drive the compressor and the load (e.g. electric generator). The exhaust gases leave the turbine at a considerable temperature (450-600C), which makes high-temperature heat recovery ideal. This is effected by a heat recovery boiler of single-pressure or double-pressure, for more efficient recovery of heat. Triple-pressure is also possible but not very usual, because it makes the system more complex and expensive, which is not always justified.

The steam produced can have high quality (i.e. high pressure and temperature), which makes it appropriate not only for thermal processes but also for driving a steam turbine thus producing additional power. In the latter case a combined cycle system is obtained, which is described in Chapter Error: Reference source not found.

Instead of producing steam, the exhaust gases after the turbine can be used directly in certain thermal processes, such as high-temperature heating and drying.

#### Closed-cycle gas turbine cogeneration systems

In the closed-cycle system (Figure 1), the working fluid (usually helium or air) circulates in a closed circuit. It is heated in a heat exchanger before entering the turbine, and it is cooled down after the exit of the turbine releasing useful heat. Thus, the working fluid remains clean and it does not cause corrosion or erosion.

Figure 1: Cogeneration system with closed-cycle gas turbine

Source of heat can be the external combustion of any fuel, even city or industrial wastes. Also, nuclear energy or solar energy can be used.

Systems of this type with a power output of 2–50 MWe operate in Europe and Japan, but their number is rather small.

Page 21

### Thermodynamic Performance of Gas Turbine Cogeneration Systems

#### Efficiency and PHR at rated power

The nominal electric efficiency (i.e. the efficiency at rated power) of small to medium gas turbine systems is usually in the range of 25–35%. Larger systems built recently have reached electric efficiencies of 40–42% by means of high temperature of exhaust gases at the turbine inlet (1200-1400C). The total efficiency is typically in the range of 60–80%. The power to heat ratio (PHR) is in the range 0.5–0.8.

Page 25

## RECIPROCATING INTERNAL COMBUSTION ENGINE COGENERATION SYSTEMS

Reciprocating internal combustion engines have high efficiencies, even in small sizes. They are available in a variety of sizes in a broad range (75 kW–50 MW). They can use a broad variety of gaseous and liquid fuels, and have good availability (80–90%). These characteristics have made them the first choice, up to now, for cogeneration applications in the institutional, commercial and residential sector, as well as in the industrial sector when low to medium voltage is required.

### Types of Reciprocating Internal Combustion Engine Cogeneration Systems

One way to classify the systems is based on the internal combustion engine cycle: Otto cycle and Diesel cycle. In an Otto engine, a mixture of air and fuel is compressed in each cylinder and the ignition is caused by an externally supplied spark. In a Diesel engine, only air is compressed in the cylinder and the fuel, which is injected in the cylinder towards the end of the compression stroke, ignites spontaneously due to the high temperature of the compressed air.

Otto engines can operate on a broad range of fuels such as gasoline, natural gas, propane, sewage plant gas, landfill methane. They are often called “gas engines”, if they use gaseous fuel. Diesel engines operate on higher pressure and temperature levels, and for this reason heavier fuels are used: Diesel oil, fuel oil and, in large two-stroke engines, residual fuel oil.

Another classification of the cogeneration system is based on the size of the engine:

- Small units with a gas engine (15–1000 kW) or Diesel engine (75–1000 kW).

- Medium power systems (1–6 MW) with gas engine or Diesel engine.

- High power systems (higher than 6 MW) with Diesel engine.

Gas engines of the following types are commercially available.

- Gasoline engines of cars, converted to gas engines. Usually, they are small engines (15–30kW), light, with high power to weight ratio. The conversion has a rather small effect on efficiency, but it decreases the power output by about 18%. Mass production results in low cost of the engines, but their life cycle is relatively short (10000–30000 hours).

- Diesel engines of cars, converted to gas engines. Their power is up to about 200 kW. Conversion is necessary on pistons, cylinder heads and valve mechanism, which are imposed by the fact that ignition will be effected not by compression only but by a spark. Conversion usually does not cause power reduction, because it is possible to adjust the excess air properly.

- Stationary engines converted to gas engines or originally designed and built as gas engines. They are heavy duty engines manufactured for industrial or marine applications. The power output reaches 3000 kW. Their robustness increases the initial cost, but reduces maintenance needs and prolongs the life cycle (15–20 years). They are capable of running continuously at high load.

- Dual-fuel stationary engines. They are Diesel engines with a power output of up to 6000 kW. Natural gas is the main fuel, which is ignited not by a spark, but by injection of Diesel oil towards the end of the compression stroke. Of the total fuel energy required, about 90% is provided by the natural gas and 10% by the Diesel oil. They also can have the capability to operate either with the aforementioned dual fuel or with Diesel oil only, which, of course, increases the capital and maintenance cost.

FUEL

Page 26

Regarding fuels of gas engines, landfill gas and sewage gas are of particular importance as a means not only of resource utilisation but also of environmental protection. Both landfill gas and sewage gas are very well suited for the operation of gas engines, since the knock-resistant methane and the high content in CO2 permit a methane number of over 130. Another opportunity to utilise the energy potential of waste is through the process of pyrolysis (decomposition of substances by heat). The resultant pyrolysis gas can be used in a gas engine.

One of the most important properties regarding the use of gas in a gas engine is its knock resistance. This is rated according to the methane number. Highly knock-resistant methane has a methane number of 100. In contrast to this, butane has a methane number of 10 and hydrogen with a methane number of 0 lies at the bottom of the scale (Table 1).

Table 1: Methane number of gaseous fuels

| Fuel |  | Methane |
| --- | --- | --- |
| Name | Composition | number |
| Hydrogen | H2 | 0 |
| Methane | CH4 | 100 |
| Ethylene | C2H4 | 15 |
| Ethane | C2H6 | 43.7 |
| Propylene | C3H6 | 18.6 |
| Propane | C3H5 | 33 |
| Butane | C4H10 | 10 |
| Carbon monoxide | CO | 75 |
| Natural gas (Typical) | CH4 88.5 % C2H6 4.7 % C3H6 1.6 % C4H10 0.2 % N2 5.0 % | 72-98 |
| Sewage gas | CH4 65 % CO2 35 % | 134 |
| Landfill gas | CH4 50 % CO2 40 % N2 10 % | 136 |