Feasibility study  Page 74

The aforementioned adverse effects may pose a problem in urban areas. In order to minimise these effects on the population, certain prerequisites should be satisfied if a cogeneration system is to be installed and operated inside a building or, in general, in urban areas:

- Careful selection of the site.

- Selection of cogeneration technology with low emissions of pollutants.

- Installation of pollution abatement and control equipment.

- Installation of elastic foundation and sound insulation and attenuation (Chapter 1.1.1).

- Construction of a stack higher than the surrounding buildings.

- Provision for safe collection and removal of liquid and solid wastes.

These measures may be costly in certain cases, and the persons involved may tend to ignore or avoid them. In order to prevent the consequences, a strong permit review process should be established by the government or the municipality.

Fuel cells are expected to be much more user and environment friendly, thanks to their much lower emissions and noise level.

### Noise and Vibration

### Page 75

Source of noise is not only the cogeneration system but also the increased traffic related to the erection and operation of the system (e.g. trucks supplying the system with fuel and/or other material, and removing wastes). Careful scheduling is perhaps the only way of reducing nuisance from traffic. Specific measures can be taken to reduce the noise coming from the system itself.

Cogeneration units have to comply with existing regulations, which specify maximum levels for noise emissions in order to protect people who live or work nearby. A couple of examples are given below

- Limit noise in the room itself using an acoustic enclosure, which will reduce the noise by at least 25 dB(A). Use acoustic dampers in the combustion air inlet channel. Use noise-absorbing materials on the walls.

- Limit noise to rooms in the immediate vicinity. Reinforce the construction of walls, ceilings and floors. Limit the number of windows and doors to a minimum.

- Limit noise to the outside. Use acoustic dampers on the exhaust gas channels.

## EFFECTS OF COGENERATION ON AIR QUALITY

The most important issue regarding the environmental impacts is whether cogeneration improves or degrades air quality. This issue is especially critical in urban areas, where air quality may be lower than the national average, and the tolerance for additional emissions may be small.

### Exhaust Gas Emissions

The components of the exhaust gases, which are of concern because they are hazardous, are the following:

- carbon dioxide (CO2),

- carbon monoxide (CO),

- nitrogen oxides (NOx),

- sulfur oxides (SOx, usually sulfur dioxide: SO2),

- unburned hydrocarbons (CxHy, also symbolised with the letters HC or UHC),

- solid particles, called also “particulates”.

Laws and regulations specify maximum emission levels for power plants. They usually are applicable for cogeneration systems too. Some countries may have a special legislation for cogeneration systems.

#### CO2 Emissions

Carbon dioxide emissions depend primarily on the type, quality and quantity of the fuel used. To a satisfactory approximation, complete combustion can be assumed, which is very close to reality, when combustion takes place with excess air and the combustion equipment is in good condition and adjusted correctly. Then, the quantity of the emitted CO2 is calculated by the equation

(5.1)

where			(5.2)

(5.3)

mass of emitted CO2,

emissions of CO2 per unit mass of fuel (e.g. kg CO2/kg fuel),

c	mass content of carbon in fuel (e.g. kg C/kg fuel),

mf	mass fuel consumption,

E	useful energy produced by the system,

	efficiency of the system, based on the lower heating value of fuel,

Hu	lower heating value of fuel.

Equations (5.1) – (5.3) are applicable not only to cogeneration systems, but to any system burning fuel. For example, when they are applied to a power plant or a cogeneration system, E is the electricity produced and  is the electrical efficiency, e, as defined by Eq. (2.3). If they are applied to a boiler, E is the useful thermal output of the boiler, Q, and  is its thermal efficiency, Q as it appears in Eq. (2.16). Typical values of c,  and Hu for various fuels are given in Table 5.1.

It has to be clarified that if the values of the parameters appearing in Eqs. (5.2) and (5.3) change for any reason (e.g. change in efficiency due to partial load, change in quality and consequently in c and Hu of fuel), then the total CO2 emitted during a period of time results as an integral over time (or summation over various times intervals) of Eq. (5.1).

Reduction of CO2 emissions

The only way to decrease the CO2 produced for a certain quantity of useful energy production is to increase the efficiency of the fuel utilization (if the fuel remains the same). However, the quantity of CO2 finally released to the environment would be lower than the one produced, if CO2 could (at least partially) be used in a process. Large-scale applications, perhaps not easily combined with cogeneration, include the enhancement of crude oil and coal recovery from oil wells and coal mines, respectively. Also, CO2 can be used with hydrogen for production of synthetic hydrocarbons. More close to cogeneration applications is the use of CO2 for enhancing the growth rate of plants cultivated in greenhouses.

#### NOx Emissions

Nitrogen oxides are formed in the combustion process from nitrogen chemically bound in the fuel or present in the air. It is the pollutant that causes the greatest concern and legislative attention; the toxic effects of NOx occur at concentrations which are at least 10 times lower than the levels at which CO becomes toxic.

The most important parameters that determine the level of NOx formation in a Diesel or gas engine are

- the combustion temperature in the primary zone of combustion chamber,

- the retention time in the primary combustion zone,

- the combustion pressure,

- the mixing rate of air and fuel.

The stoechiometric air ratio

(5.4)

often called “lambda ratio” for convenience, has a direct or indirect effect on the aforementioned parameters and, consequently, on the NOx emissions

Page 91

## ECONOMIC AND SOCIAL IMPACTS

Page 91

Cogeneration has attracted attention not only for its benefits or adverse effects on energy efficiency, the environment, and utility planning and operations, but also for its possible implications on the economic and political institutions traditionally involved in the supply and demand of electrical and thermal energy. Many analysts feel that, as global reserves of oil and natural gas dwindle, major changes must occur in the technical, economic, and institutional context for energy supply and demand in industrialised societies. Cogeneration is likely to be a part of these energy system changes.

Cogeneration may also benefit the national economy, if it results in reduction of the total expenses for imported fuels. Furthermore it may have important social and economical implications in sectors such as business development patterns, and the role of policies in energy supply; they are briefly outlined in the following.

- As advanced cogeneration technologies with greater fuel flexibility emerge, new business opportunities should arise for supplying alternate fuels such as municipal solid waste, biomass, synthetic liquid and gaseous fuels. These opportunities can be captured not necessarily by the existing utilities, but by local authorities (municipalities) or private entrepreneurs.

- Cogenerators will more likely purchase a complete cogeneration system from vendors acting as intermediaries between manufacturers and purchasers. These vendors will be able to offer a wider range of packaged systems than a single manufacturer, and to tailor the system to a user’s specific needs. They also may evolve as total service companies offering repair and maintenance too.

- Cogeneration may need financial assistance. Traditional lending institutions such as banks could become financiers for this type of projects, but new schemes such as Third Part Financing (TPF) companies can be established.

It is usual that central power plants are built in large sizes and located in remote areas. Construction and operation of these plants causes a relocation of many working persons from their hometown to the place of the plant. Conversely, cogeneration units are of smaller size and are installed more close to inhabited areas. Their dispersion in many places creates new job opportunities locally. As a result the work force remains in the area, and the whole activity related with the construction, operation and maintenance of the cogeneration system, as well as with the opportunities potentially created due to the availability of electricity and heat, contributes to the economic development of the local society.

Page 92

# ECONOMIC ANALYSIS OF COGENERATION SYSTEMS

In addition to being energy efficient, a cogeneration system must be economically viable in order to proceed with the investment. In this chapter, information for capital, operation and maintenance costs of cogeneration systems is given, criteria of economic performance are defined, a procedure for economic assessment is developed, and application examples are presented. It must be emphasised that cost information given here is indicative and it can be used for first estimates only. Furthermore, cost changes with time. Therefore, the final decisions should be based on cost data provided by companies which will supply, install and, perhaps, maintain the equipment.

## COST OF COGENERATION SYSTEMS

In order to perform a feasibility study or an economic analysis, there is need to know the cost for constructing and operating a system. Related information is given in this chapter.

### Investment Cost

Investment cost is also called capital cost or initial cost or first cost. It consists of equipment cost, installation cost, and “soft” (called also “project” or “engineering and management”) costs.

#### Equipment costs

Equipment costs consist of the cost for purchase of the equipment, including any taxes, and transportation on the site. They depend on the components comprising the system and their particular specifications. The most important of those are the following.

- Prime mover and generator set.  Power output, alternative fuel capability, generator voltage, emission control techniques in prime mover, noise reduction.

- Heat recovery and rejection system.  Required media (steam, hot or chilled water), quality of thermal energy (pressure and temperature), number of pressure and temperature levels required, emission control equipment, water treatment unit.

- Supplementary firing.  Additional thermal capacity, alternative fuel capability.

- Exhaust gas system and stack.  Exhaust gas temperature, single or multiple stacks for multiple engines, emission control equipment, need for bypass valve.

- Fuel supply.  Interconnection with fuel supply system, storage capability, fuel metering; in particular for natural gas, need for compressor, if the line pressure has to be increased.

- Control board.  Extent of automation, requirements for unattended operation, inter-connection with the user’s facility.

- Interconnection with the electric utility.  Connection line, one- or two-way connection, safety and metering equipment.

- Piping.  Connection with the water, steam, compressed air (if needed) circuits.

- Ventilation and combustion air systems.  Ducts, filters, sound attenuation equipment.

- Shipping charges.

- Taxes, if applicable.

#### Installation costs

They consist of:

- Installation permits,

- Land acquisition and preparation,

- Building construction,

- Installation of equipment,

- Documentation and as-built drawings.

Some of these costs may not be applicable, e.g. if the space is already available for the cogeneration system.

#### “Soft” (or project) costs

Design and professional service fees for the analysis, planning and development of a cogeneration system are frequently referred to as soft costs. They may be in the range of 15-30% of the equipment and construction cost. The most significant professional fees and other costs are the following.

- Architectural / engineering design fees.

- Construction management fees.

- Environmental studies and permitting costs.

- Special consultants and inspectors.

- Legal fees.

- Letters of credit.

- Training.

Additional costs may incur under certain financial arrangements (e.g. interest paid during construction, bank fees, debt insurance).

In budget estimates, a contingency or allowance for unforeseen costs is taken into consideration. Early in the design process, the contingency may be in the range of 15-20%. At the completion of the design, when uncertainty is reduced, the contingency may be reduced to 5%. Examples of investment costs breakdown are given in the following tables:

Table 1: Breakdown of investment costs for small-scale cogeneration [Jennekens, 1989].

| Type of cost | % of total |
| --- | --- |
| Cogeneration unit including heat recovery equipment Instrumentation, regulation and control Auxiliary systems Connection to grid Civil work and/or acoustic enclosure Installation and commissioning Project costs | 55 15 5 5 10 5 5 |
| Total | 100 |

Table 2: Examples of breakdown of investment costs for a gas turbine and a steam turbine cogeneration system [Belding, 1982].

| Type of cost | % of total |  |
| --- | --- | --- |
|  | Gas-turbine(1) | Steam-turbine(2) |
| Turbinen-Generator Heat recovery steam generator Instrumentation, regulation, control Auxiliary systems Connection to grid Civil work (land, buildings, roads) Engineering and construction management Contingency | 34 20 4 7 3 6 11 15 | 50 (3) - 3 4 6 11 11 15 |
| Total | 100 | 100 |
| - Nominal power 10 MW. - Non-condensing turbine. Nominal power 30 MW. - Boiler cost is included. |  |  |

Figure 1: Specific investment cost of small-scale cogeneration systems with reciprocating internal combustion engine.

It is evident that the investment cost of a cogeneration project depends on a lot of factors, which characterise the particular project. Any generalised costs cannot be useful but only for an initial and very rough estimate. For this purpose, cost information published in the literature has been used to draw the graphs appearing in Figure 1 - Error: Reference source not found -. Costs obtained form these figures may have an uncertainty of ± (20-25)%. In Figure 1 in particular, dotted lines indicate the uncertainty zone.

### Operation and Maintenance Costs

Operation and maintenance costs depend to a certain extent on decisions taken at the design and construction phase of the system. It is possible that actions reducing the initial cost may lead to increased operation and maintenance costs, with a negative impact on the total economic performance of the project. The major operation and maintenance costs are the following.

## PROCEDURE FOR ECONOMIC ANALYSIS OF COGENERATION SYSTEMS

Page 99  to 110

The measures defined in chapter Error: Reference source not found are used to assess the economic viability and performance of an investment in a cogeneration system, as well as to compare investments in alternative systems. In order to calculate the value of each measure using the equations of the previous chapter, there is need to estimate (a) the initial cash flow, F0, and (b) the net cash flow Ft in year t  1. A procedure for these estimates is presented in the following.

### Initial Cash Flow (F0)

Vendor quotations or information from other sources (e.g. Chapter 2.1) is used to estimate the investment cost C of the system, where C is considered as the present worth of the cost (time t = 0). If there is need, instructions given in Chapter Error: Reference source not found can be used to determine the present worth of costs occurring during the years of construction.

In certain countries, investment grants are provided for promotion of cogeneration. They are given with no obligation on cogenerator’s side, other than observing certain standards, in particular regarding the real operating efficiency of the system. In addition, the investor may borrow a certain amount of money from a bank or another institution. In order to take these possibilities into consideration, it is written

(6.26)

where

C	investment cost of the system,

Cg	amount of grant,

L	amount of loan,

cg	grant as a fraction of the investment cost: cg = Cg/C,

loan as fraction of the investment cost: = L/C.

Of course, zero values for Cg or L are acceptable and do not cause any problems with the rest of the calculations.

### Net Cash Flow for the Years of Analysis (Ft, t  1)

#### Annual operation profit

The operation of a cogeneration system causes expenses, but it also results in savings (avoided cost of electricity that otherwise would be purchased from the grid and heat that would be produced by a boiler), and also in revenues, if excess electricity is sold. The annual operation profit of the cogeneration system is defined as

(6.27)

where

Ce	avoided cost of electricity, i.e. cost of electricity that, if not cogenerated, it would be purchased from the grid,

Re	revenue from selling excess electricity, if any,

Ch	avoided cost of heat, i.e. cost of heat that, if not cogenerated, would be produced by boiler(s),

Cf	cost of fuel for the cogeneration system,

Com	operation and maintenance cost (except fuel) of the cogeneration system.

Subscript t indicates the year (t = 1, 2, …, N).

The avoided cost of electricity, Ce, is a function of the cogenerated electricity which is consumed on site, and on the tariff structure for electricity supplied by the grid, which may consider not only energy, but also power, power factor, time of the day, peak demand, etc. A cost component which is often overlooked, but it may be non-negligible, is an increase of the electricity bill due to taxes: utilities often include some tax imposed on behalf of a government body (state and/or local municipality). For example, such a tax of 8% on the total cost of electricity is imposed on apartments in Athens. Since all these parameters are site-specific, it is not possible to give a general expression for Ce here.

The revenue Re from excess electricity sold to the grid or to a third party is a function of the electrical energy and of the tariff structure for electricity sold to the grid or of the agreement between the parties involved. For the same reasons as with Ce, no general expression for Re will be attempted here.

The avoided cost of heat includes cost of fuel for the boiler that would produce the thermal energy, if not cogenerated, as well as other operation and maintenance expenses for the boiler and related auxiliary equipment. The fuel cost is a function of the fuel quality and the fuel tariff structure. In the simplest case, where a constant unit cost of fuel applies, the cost of fuel for the boiler during a year is calculated by:

(6.28)

where

cfB	cost per unit mass of fuel for the boiler,

mfB	mass of fuel that would be consumed by the boiler during the year,

useful thermal power at a certain instant of time,

Q	annual useful thermal energy produced by the cogeneration system,

HuB	lower heat value of fuel for the boiler,

efficiency of the boiler,

annual average values of HuB and , respectively.

Capital cost of boiler is usually not taken into consideration, because it is assumed that a boiler would be installed anyway for back up. However, if this is not the case, then the capital cost of boiler should be included.

The cost of fuel for the cogeneration system is a function of the fuel quantity and the fuel tariff structure. If a constant unit cost can be assumed, then it can be written

(6.29)

where

cf	cost per unit mass of fuel for the cogeneration system,

mf	annual fuel consumption of the cogeneration system,

electric power output at a certain instant of time,

Hu	lower heating value of fuel for the cogeneration system,

electrical efficiency at load of the cogeneration system.

The last term in Eq. (6.29) substitutes the integral with a summation over periods of time ti defined so that in each period i a steady-state operation at power can be assumed. The number of periods can be as large as necessary for an accurate estimation of fuel consumption.