Learning Outcome 1

# DEFINITION AND HISTORICAL DEVELOPMENT OF COGENERATION

Ref Page (7)

The usual (conventional) way to cover needs in electricity and heat is to purchase electricity from the local grid and generate heat by burning fuel in a boiler, a furnace, etc. However, a considerable decrease in total fuel consumption is achieved, if cogeneration (known also as combined heat and power, CHP) is applied.

Cogeneration is the thermodynamically sequential production of two or more useful forms of energy from a single primary energy source.

The two most usual forms of energy are mechanical and thermal energy. Mechanical energy is usually used to drive an electric generator. This is why the following definition, even though restrictive, often appears in the literature:

Cogeneration is the combined production of electrical (or mechanical) and useful thermal energy from the same primary energy source.

The mechanical energy produced can be used also to drive auxiliary equipment, such as compressors and pumps. Regarding the thermal energy produced, it can be used either for heating or for cooling. Cooling is effected by an absorption unit, which can operate through hot water, steam or hot gases.

During the operation of a conventional power plant, large quantities of heat are rejected in the atmosphere either through the cooling circuits (steam condensers, cooling towers, water coolers in Diesel or Otto engines, etc.) or with the exhaust gases. Most of this heat can be recovered and used to cover thermal needs, thus increasing the efficiency from 30-50% of a power plant to 80-90% of a cogeneration system. A comparison between cogeneration and the separate production of electricity and heat from the point of view of efficiency is given in Error: Reference source not found, based on typical values of efficiencies.

# PERFORMANCE INDICES OF COGENERATION SYSTEMS

Ref Page 9

Before proceeding with the description of cogeneration technologies, it is necessary to define certain indices, which reveal the thermodynamic performance of a cogeneration system and facilitate the comparison of alternative solutions (systems). Numerous indices have appeared in the literature. The most important of those are defined in this chapter:

Efficiency of the prime mover (e.g. of gas turbine, Diesel engine, steam turbine):

(2.1)

where

Ws	shaft power of the prime mover

Hf	fuel power (flux of the fuel energy) consumed by the system:

Hf = mfHu		(2.2)

mf	fuel mass flow rate,

Hu	lower heating value of fuel.

Electrical efficiency:

(2.3)

where  is the net electric power output of the system, i.e. the electric power consumed by auxiliary equipment has been subtracted from the electric power of the generator.

Thermal efficiency:

(2.4)

where  is the useful thermal power output of the cogeneration system.

Total energy efficiency of the cogeneration system:

(2.5)

The quality of heat is lower than the quality of electricity and it is decreasing with the temperature at which it is available.

Even though energy efficiencies are most commonly used up to now, a thermodynamically more accurate evaluation and a more fair comparison between systems can be based on exergetic efficiencies defined in the following

Ref Page 10/11

Exergetic thermal efficiency:

(2.6)

where

flux of energy corresponding to ,

flux of fuel exergy:

(2.7)

specific exergy (exergy per unit mass) of fuel.

Total exergetic efficiency:

(2.8)

Power to heat ratio:

(2.9)

Fuel energy savings ratio:

(2.10)

where

total fuel power for separate production of  and ,

fuel power of the cogeneration system producing the same amounts of  and .

In order for a cogeneration system to be a rational choice from the point of view of energy savings, it must be FESR > 0.

Equations (2.3)-(2.5) and (2.9) lead to the following relations:

(2.11)

(2.12)

Equations (2.11) and (2.12) help in determining acceptable values of the power to heat ratio, when the electrical efficiency of a system is known, given the fact that the total efficiency does not exceed typically 90%.

Example 2.1. Let  and 0.65  0.90. 	Then, Eq. (2.12) results in the range: 1.6  PHR  0.8.

It should be mentioned that the power to heat ratio is one of the main characteristics for selecting a cogeneration system for a particular application.

If it can be considered that a cogeneration system substitutes separate units of electricity and heat production with efficiencies  and , respectively, then it can be proved that

(2.13)

It can be written

(2.14)

(2.15)

(2.16)

where the subscripts W and Q denote the separate production of electricity and heat (e.g. by a power plant and a boiler), respectively.

Example 2.2	A cogeneration system with a total efficiency Q = 0.80 and a power to heat ratio PHR = 0.6 substitutes a power plant of efficiency  and a boiler of efficiency . Then, Eq. (2.13) gives FESR = 0.325, i.e. the cogeneration reduces the total energy consumption by 32,5%.

All the previous equations are valid also if power is replaced by energy in a certain period of time; then, integral values of the indices are obtained, which reveal the performance of the system over this period. For example, Eq. (2.5) can be written

(2.5)a

where

electric energy produced by the cogeneration system during a year,

thermal energy produced during a year,

energy of fuel consumed during a year.

Thus, Eq. (2.5)a gives the annual total efficiency  of the cogeneration system.

Page 12

# CONTEMPORARY COGENERATION TECHNOLOGIES

Most cogeneration systems can be characterised either as topping systems or as bottoming systems. In topping systems, a high temperature fluid (exhaust gases, steam) drives an engine to produce electricity, while low temperature heat is used for thermal processes or space heating (or cooling).

In bottoming systems, high temperature heat is first produced for a process (e.g. in a furnace of a steel mill or of glass-works, in a cement kiln) and after the process hot gases are used either directly to drive a gas-turbine generator, if their pressure is adequate, or indirectly to produce steam in a heat recovery boiler, which drives a steam-turbine generator.

Indicative temperature ranges for the two types of systems are given in Figure 1:

Figure 1: Indicative temperature ranges for topping and bottoming cogeneration systems

In the following chapters, various cogeneration technologies are described.

Page 13

## STEAM TURBINE COGENERATION SYSTEMS

A system based on steam turbine consists of three major components: a heat source, a steam turbine and a heat sink. The system operates on the Rankine cycle, either in its basic form or in its improved versions with steam reheating and regenerative water preheating. Most of the generation capacity installed since the early 1900’s is based on systems of this type.

The most common heat source is a boiler, which can burn any type of fuel or certain combinations of fuels, and produces superheated steam. In place of a boiler, nuclear reactors can be used. On the other hand, the system can use renewable energy such as biomass or concentrated solar radiation. Even waste by-products can be burned, provided the boiler is equipped with proper pollution abatement units.

The operating conditions can vary in a wide range. For cogeneration applications, steam pressure can range from a few bars to about 100 bar; in the utility sector, higher pressures can also be used. Steam temperature can range from a few degrees of superheat to about 450C, and, in the utility sector, to about 540C. The power output is usually in the range of 0.5-100 MW, even though higher power is also possible.

Steam turbine systems have a high reliability, which can reach 95%, high availability (90-95%) and long life cycle (25-35 years). The installation period is rather long: 12-18 months for small units, up to three years for large systems.

Figure 2: Cogeneration system with back-pressure steam turbine

Page 14/ 15

#### Condensing steam turbine systems

In such a system, steam for the thermal load is obtained by extraction from one or more intermediate stages at the appropriate pressure and temperature (Figure 3). The remaining steam is exhausted to the pressure of the condenser, which can be as low as 0.05 bar with corresponding condensing temperature of about 33C.

Figure 3: Cogeneration system with condensing steam turbine

### Thermodynamic Performance of Steam Turbine Cogeneration Systems

Page 17

#### Efficiency and PHR of steam turbine systems

The total energy efficiency is relatively high (60–85%) and decreases only slightly at partial load. However, the electrical efficiency is low (values in the range 15–20% are not seldom), which results in low power to heat ratio (PHR = 0.1–0.5). In general, the higher the temperature required for process steam is, the lower the electrical efficiency is. The electrical efficiency can be increased to a certain extent by increasing the pressure and temperature of steam at the turbine inlet.

Back-pressure steam turbine systems.

When all the thermal energy of steam is utilised and the condensate returns from the processes with no supplementary cooling and no heat rejected to the environment, the total efficiency may reach 85%. Since the generated electrical power is proportional to the steam flow rate towards the process, the value of the power to heat ratio, PHR, remains approximately constant during load changes.

Condensing steam turbine systems.

The heat rejected through the condenser results in a lower total efficiency. Main advantage of these systems is the capability to change the electrical and thermal power independently, inside certain limits, and consequently to change the value of PHR.

Bottoming cycle steam turbine systems.

The electrical efficiency is typically in the range 5–15%. This is a low value, but it is important that electricity is produced from thermal energy, which otherwise would be rejected to the environment.

#### Partial load operation of steam turbines

Optimum performance of a steam turbine typically occurs at approximately 95% of the rated power. Since most turbines used in cogeneration systems are multistage devices designed for a specific application, often having both condensing and extraction capabilities, the part-load characteristics are unique to each turbine.

## GAS TURBINE COGENERATION SYSTEMS

Page 18

Gas turbines either in a simple cycle or in a combined cycle (Chapter 3.2) are the most frequently used technology in recent cogeneration systems of medium to high power. Their electric power output ranges from a few hundred kilowatts to several hundred megawatts. On the other side of the spectrum, recent research and development aims at the construction of micro turbines, which have a power output of a few kilowatts.

### Gas Turbine Cycles

A gas turbine can operate either in open cycle or in a closed cycle.

#### Open-cycle gas turbine cogeneration systems

Most of the currently available gas turbine systems in any sector of applications operate on the open Brayton (also called Joule cycle when irreversibilities are ignored) (Error: Reference source not found): a compressor takes in air from the atmosphere and derives it at increased pressure to the combustor. The air temperature is also increased due to compression. Older and smaller units operate at a pressure ratio in the range of 15:1, while the newer and larger units operate at pressure ratios approaching 30:1.