## Slide 1: Fire Protection
OSHA Part 1910 Subpart L

## Slide 2: Fire Protection Objectives
Familiarization with Subpart L
Define key terms
Discuss fire brigades
Discuss use of fire extinguishers
Discuss other fire extinguishing systems
Discuss where to get additional information

## Slide 3: Standards
1910.155 - Scope, application and definitions
1910.156 - Fire Brigades
1910.157 - Portable Fire Extinguishers
1910.158 - Standpipe and Hose Systems
1910.159 - Automatic Sprinkler Systems
1910.160 - Fixed Extinguishing Systems, general

## Slide 4: Standards
1910.161 - Fixed Extinguishing Systems, Dry Chemical
1910.162 - Fixed Extinguishing Systems, Gaseous Agent
1910.163 - Fixed Extinguishing Systems, Water Spray and Foam
1910.164 - Fire Detection Systems
1910.165 - Employee Alarm Systems

## Slide 5: Standards
1910 Subpart L - Authority for 1910 Subpart L
1910 Subpart L - Appendix A
  Fire Protection
1910 Subpart L - Appendix B
  National Consensus Standards

## Slide 6: Standards
1910 Subpart L - Appendix C
  Fire Protection References and Other Information
1910 Subpart L - Appendix D
1910 Subpart L - Appendix E
  Test Methods for Protective Clothing

## Slide 7: Fire Tetrahedron
Basic components of a fire are:
  fuel
  source of ignition
  oxygen
  process of combustion
Commonly referred to as the "fire tetrahedron"

## Slide 8: 1910.155 Scope, application and definitions
Scope
This subpart contains requirements for fire brigades, and all portable and fixed fire suppression equipment, fire detection systems, and fire or employee alarm systems installed to meet the fire protection requirements of 29 CFR Part 1910.

## Slide 9: 1910.155 Scope, application and definitions
Application.
This subpart applies to all employments except for maritime, construction, and agriculture.
Definitions applicable to this subpart.

## Slide 10: 1910.155 Scope, application and definitions
"Approved”
  means acceptable to the Assistant Secretary under the following criteria:
  If it is accepted, or certified, or listed, or labeled or otherwise determined to be safe by a nationally recognized testing laboratory

## Slide 11: 1910.155 Scope, application and definitions
"Class A fire" means a fire involving ordinary combustible materials such as paper, wood, cloth, and some rubber and plastic materials.

## Slide 12: 1910.155 Scope, application and definitions
"Class B fire" means a fire involving flammable or combustible liquids, flammable gases, greases and similar materials, and some rubber and plastic materials.

## Slide 13: 1910.155 Scope, application and definitions
"Class C fire" means a fire involving energized electrical equipment where safety to the employee requires the use of electrically nonconductive extinguishing media.

## Slide 14: 1910.155 Scope, application and definitions
"Class D fire" means a fire involving combustible metals such as magnesium, titanium, zirconium, sodium, lithium and potassium.

## Slide 15: Fire/Life Safety Fire Protection
Class A Fires: Ordinary combustibles such as wood and paper.
Class B Fires: Flammable and combustible liquids and gases.
Class C Fires: Energized electrical equipment.
Class D Fires: Combustible metals.
Class K Fires: Cooking Oils and Fats.

## Slide 16: 1910.155 Scope, application and definitions
"Extinguisher classification" means the letter classification given an extinguisher to designate the class or classes of fire on which an extinguisher will be effective.

## Slide 17: 1910.155 Scope, application and definitions
"Extinguisher rating" means the numerical rating given to an extinguisher which indicates the extinguishing potential of the unit based on standardized tests developed by Underwriters' Laboratories, Inc.

## Slide 18: 1910.155 Scope, application and definitions
"Fire brigade" (private fire department, industrial fire department) means an organized group of employees who are knowledgeable, trained, and skilled in at least basic fire fighting operations.

## Slide 19: 1910.155 Scope, application and definitions
"Fixed extinguishing system" means a permanently installed system that either extinguishes or controls a fire at the location of the system.

## Slide 20: 1910.155 Scope, application and definitions
"Incipient stage fire" means a fire which is in the initial or beginning stage and which can be controlled or extinguished by portable fire extinguishers, Class II standpipe or small hose systems without the need for protective clothing or breathing apparatus.

## Slide 21: 1910.155 Scope, application and definitions
"Interior structural fire fighting" means the physical activity of fire suppression, rescue or both, inside of buildings or enclosed structures which are involved in a fire situation beyond the incipient stage.

## Slide 22: 1910.155 Scope, application and definitions
"Multipurpose dry chemical" means a dry chemical which is approved for use on Class A, Class B and Class C fires.

## Slide 23: 1910.155 Scope, application and definitions
"Positive-pressure breathing apparatus" means self-contained breathing apparatus in which the pressure in the breathing zone is positive in relation to the immediate environment during inhalation and exhalation.

## Slide 24: 1910.155 Scope, application and definitions
"Sprinkler system" means a system of piping designed in accordance with fire protection engineering standards and installed to control or extinguish fires. The system includes an adequate and reliable water supply, and a network of specially sized piping and sprinklers which are interconnected. The system also includes a control valve and a device for actuating an alarm when the system is in operation.

## Slide 25: 1910.156 Fire Brigades
This section contains requirements for:
  Organization
  Training
  Personal Protective Equipment

## Slide 26: 1910.156 Fire Brigades
Organization
  Employer shall prepare and maintain a written policy statement which:
    Establishes the fire brigade and its organizational structure
    Defines the functions to be performed; and
    States training program requirements.
      The employer must assure that employees who are expected to do interior structural firefighting are physically capable of performing duties

## Slide 27: 1910.156 Fire Brigades
Training and Education
  Shall be conducted prior to assignment
  At least annually
  Quarterly training or education sessions are required for fire brigades expected to perform interior structural fire fighting.

## Slide 28: 1910.156 Fire Brigades
Fire Fighting Equipment
  The employer shall maintain and inspect, at least annually, fire fighting equipment to assure safe operational condition of the equipment.
  Portable fire extinguishers shall be inspected at least monthly
  Respirators shall be inspected at least monthly

## Slide 29: 1910.156 Fire Brigades
Protective Clothing
  These requirements apply to those employees who perform interior structural fire fighting.
  These requirements do not apply to employees who use fire extinguishers or standpipe systems to fire incipient level fires.

## Slide 30: 1910.156 Fire Brigades
Protective Clothing
  Foot and leg protection
  Body protection
  Hand Protection
  Head, eye and face protection

## Slide 31: 1910.156 Fire Brigades
Respiratory Protection Devices
  The employer shall assure that respiratory protection devices worn by fire brigade members meet the requirements of 1910.134
    A minimum rating of 30 minutes
    Requires use of 2 in 2 out rule

## Slide 32: 1910.157 Portable Fire Extinguishers
Requirements
  Placement
  Use
  Maintenance
  Testing

## Slide 33: Portable Fire Extinguishers
If portable fire extinguishers are provided for employee use, the employer must mount, locate and identify them so workers can access them without subjecting themselves to possible injury.
Blocked extinguisher
Notes: <number>
<footer>
<header>
<date/time>
1910.157(c)(1)
Employers can choose whether to train their workers to fight fires or to rely on outside services.

## Slide 34: Extinguisher Classification
Class A – ordinary combustibles (wood, cloth, paper)
Class B – flammable liquids, gases, greases
Class C – energized electrical equipment
Class D – combustible metals
Letter classification given an extinguisher to designate the class or classes of fire on which it will be effective.
A
B
C
D
Ordinary
Combustibles
Combustible
Metals
Flammable
Liquids
Electrical
Equipment
Notes: <number>
<footer>
<header>
<date/time>
The class of extinguisher should be on the extinguisher shell. The picture-symbol labeling system now in use is designed to make the operation of fire extinguishers more effective and safe to use through the use of less confusing pictorial labels. The system also emphasizes when not to use an extinguisher on certain types of fires.
Because of recent information outlining the difficulties inherent in the extinguishment of fires in cooking appliances that involve combustible cooking media (vegetable or animal oils and fats), a new classification (Class K) has been established. This classification is not listed in OSHA standards. NFPA 10 specifies that listed and labeled Class K fire extinguishers are to be provided in these cases.
Class A Class B Class C Class K

## Slide 35: Extinguisher Rating
Numerical rating given to Class A and B extinguishers which indicate how large a fire an experienced person can put out with the extinguisher
Ratings are based on tests conducted at Underwriters’ Laboratories, Inc.
  Class A: 1-A, 2-A, . . . 40-A
  Class B: 1-B, 2-B, . . . 640-B
A 4-A extinguisher, for example, should extinguish about twice as much fire as a 2-A extinguisher
Notes: <number>
<footer>
<header>
<date/time>
Class C extinguishers have only a letter rating because there is no readily measurable quantity for Class C fires which are essentially Class A or B fires involving energized electrical equipment. Class D extinguishers likewise do not have a numerical rating. Their effectiveness is described on the faceplate.

## Slide 36: Maintaining Portable Fire Extinguishers
Must maintain in a fully charged and operable condition
Must keep in their designated places at all times except during use
Must conduct an annual maintenance check
Must record the annual maintenance date and retain this record for one year after the last entry or the life of the shell, whichever is less
Notes: <number>
<footer>
<header>
<date/time>
1910.157(c)(4)
1910.157(e)(3)

## Slide 37: Portable Fire Extinguisher Training and Education
Where portable fire extinguishers have been provided for employee use in the workplace, employees must be provided with an educational program on the:
  General principles of fire extinguisher use
  Hazards of incipient (beginning) stage fire fighting
Employees designated to use extinguishers must receive instruction and hands-on practice in the operation of equipment
Notes: <number>
<footer>
<header>
<date/time>
1910.157(g)
Training and education required upon initial employment/assignment and at least annually thereafter.
“Incipient Stage Fire” means a fire which is in the initial or beginning stage and which can be controlled or extinguished by portable fire extinguishers, Class II standpipe or small hose systems without the need for protective clothing or breathing apparatus. [1910.155(c)(26)]

## Slide 38: 1910.157 Portable Fire Extinguishers
  Training and Education
    Employees shall be educated in
      Use of extinguishers
      Associated Hazards
      Initially and Annually
    Employees designated to use fire fighting equipment shall be trained

## Slide 39: 1910.157 Portable Fire Extinguishers
General Requirements
  Mount, locate and identify extinguishers so that they are readily accessible
  Only approved extinguishers shall be used
  Maintain extinguishers in a fully charged and operable condition

## Slide 40: 1910.157 Portable Fire Extinguishers
Selection and Distribution
  Based on Classes of anticipated workplace fires
  On size and degree of hazard

## Slide 41: 1910.157 Portable Fire Extinguishers
  Extinguishers shall be distributed so that maximum travel distances apply:
  Class A 75 feet
  Class B 50 feet
  Class C Based on appropriate pattern
  Class D 75 feet

## Slide 42: 1910.157 Portable Fire Extinguishers
  Inspection, Maintenance and Testing
    Extinguishers shall be:
    Visually inspected monthly
    Maintained annually
    Hydrostatically tested periodically IAW Table L-1

## Slide 43: Computer Monitor Fire A computer monitor left on over a weekend caused this fire resulting in $100,000 damage.

## Slide 44: FAN FIRE $20000 Damage

## Slide 45: What’s wrong with this sprinkler head?

## Slide 46: Training Resources
United States Fire Administration (USFA)
1-800-561-3356
www.usfa.fema.org
Technical Reports
Books
CD-Roms

## Slide 47: Training Resources
National Fire Protection Association (NFPA)
1-800-344-3555
www.nfpa.org

## Slide 48: Useful Web Sites
Consumer Products Safety Commission
  www.cpsc.org
Firehouse Magazine
  www.firehouse.com

## Slide 49: Summary
This is only a small portion of Subpart L
Research the standard for standpipe and fixed system requirements.
What is a Class B fire?
Does an interior fire brigade require quarterly training?
A magnesium fire requires, what type fire extinguisher?