# Chapter 7 Practical Application

# Introduction

To illustrate the features of Chapter 7, which outlines the basic construction and theory of operation of test instruments, I am using an application that requires the interpretation of a range of test instrument specifications to satisfy the requirements of Electrical Regulations.

RCD Tester	Courtesy of Gerard Industries

Application

Electricians must use the appropriate test equipment to adequately test in accordance with AS/NZS 3000.2000. To select the appropriate test equipment, a range of test equipment and their specifications are listed below:

1. A low reading ohmmeter capable of displaying accurate readings in the range between 0.5 and 5 ohms;

2. An insulation tester, which has a nominal open circuit voltage of 500 VDC and shall maintain its terminal voltage within +20%-10% of the nominal open circuit voltage, when measuring a resistance of 1.0 megohm on the 500 V range or 10 megohms on the 1000 V range;

3. An approved proximity voltage tester or neon test pencil of at least 500 V rating, similar to the following:

(a) Encapsulated Neon;

(b) Hioki Rotary PSI;

(c) Kyoritsu Rotary Unit Cat. No. 8031;

(d) Kyoritsu (LED) Unit Cat. No. 8030.

Additional meters for specific load current:

1. A clamp on meter for measuring load current. Courtesy of Fluke.

2. A clamp on milliammeter for measuring leakage current. Courtesy of Fluke.

3. Residual Current Device (RCD) tester. Courtesy of Clipsal.

4. A fault loop impedance tester. Courtesy of Clipsal.

A fault loop impedance tester 	Courtesy of Clipsal

In each of these applications you are required to select a suitable test instrument that would satisfy the specifications of the task.

This idea of linking the terms and parameters of a practical application to chapters could also be used for the following:

- The replacement of a panel meter (pdf). This can be either a moving coil meter or a moving iron meter, courtesy of NHP and Farnell (Chapter 5);

#### Panel Meters	Courtesy of NHP & Farnell

- The installation of digital kilowatt meters (Chapter 2);

- Interpreting electrical diagrams (Chapter 17);

- As a simulated practical exercise in a classroom.

## Scope

These are common tasks undertaken by an apprentice under the supervision of a contractor or tradesperson.

## Description and extent of work

The list below is typical of the parameters that you have to measure:

- Continuity (refer to Chapter 10);

- Short circuit (refer to Chapter 2);

- Current measurement (refer to Chapter 2);

- Voltage measurement (refer to Chapter 2);

- Insulation resistance (refer to Chapter 10);

- Earth resistance (refer to Chapter 2);

- Earth voltage (refer to Chapter 2);

- Earth fault current (refer to Chapter 2);

- Resistance (refer to Chapters 2, 4 and 8);

- High resistance (refer to Chapters 2, 4 and 8);

- Polarity (refer to Chapters 3, 5 and 14).

## Regulations

Test in accordance with:

- AS/NZS 3000:2000; AS/NZS 3017:2001; AS/NZS 3008.1.1:1998; AS/NZS 3018:1997; AS/NZS 3190:1994; AS/NZS 3760:2001;

- Safety Tag and Lockout Procedures; Testing procedures for customer Installations; Installation procedures for safety switches RCDs.

## General

Consider the following when testing or choosing a meter:

- Accurate readings (refer to Chapter 7) parallax errors and specification accuracy;

- Location and connection (refer to Chapter 2) measuring in electrical circuits;

- Electrical loading (refer to Chapter 7) meter loading;

- Mounting orientation (refer to Chapter 2 panel meters and Chapter 7 tong testers.);

- Scales and Range (refer to Chapter 7);

- Before buying a Digital MultiMeter (DMM), consider not only the basic specifications, but also the features, functions, applications and overall value represented by the meter’s design. Courtesy of Fluke;

- Choosing a meter for a particular task. Courtesy of NHP;

- Comparing Digital multimeters.

References:

Jenneson, Jim, 2003, Electrical Principles for the Electrical Trades 5th edn, Sydney: McGraw-Hill Australia, Chapters 2, 3, 4, 5, 7, 8, 10, 14 and 17.

Internet references: