TQ1.1 Describe the process sequence in generating electrical energy using a coal fired thermal generating plant.  Include the main items of equipment and their function and any ancillary services e.g. cooling, scrubbing.  Start your description with the raw coal coming out of the ground and end at the power supplied to the ‘yard’ transformer

Coal and nuclear thermal power plants may take a long time to achieve a steady state power output and are thus used to supply large amounts of base-load demand.

•The voltage at which the current is produced ranges from 11 000 V to 23 000 V.

•Transformers are used to ‘step up’ the voltage for transmission and ‘step down’ for utilisation of the electrical energy.

- TQ2.1 With the aid of a diagram describe the basic principle of electricity generation in an alternator.

TQ1.3 How is the thermal efficiency of a gas turbine alternator increased?

- TQ1.4 Why is it important to drive a generator at a particular constant speed?

- To maintain the constant frequency according to the equation

- 120 f

- Ns = ---------------------

- P

- TQ1.5 Apart from being a clean energy source, what are some advantages of hydro generation over steam generation?

Hydro power is a very efficient source of renewable energy.  Hydropower systems are very efficient because of the density of water, the force of gravity and the technological advantages of today.  These systems can covert up to 90% of the energy of water into electric energy, which is an astonishing number.

With this high efficiency the cost of hydroelectricity has dropped with evolving technologies, and is estimated to be about 40% less expensive than using fossil fuels.

Since hydro power is fueled by water, it has the advantage of being only used when needed, because it is easy to control the storage and allowable flow of water into a hydro power system.

- TQ1.6 What is hot rock technology?

Hot rock' or technology is a form of geothermal energy being developed in South Australia.

•High thermal energy in rocks some 3 km below the earth's surface is being retrieved to produce steam to drive generators

- TQ1.7 How can water be reused for power generation in a hydro scheme?

- Hydel turbines, in general, allow the water to flow away after it has done its work. However, in peak-power generation schemes, water stored in reservoirs flows down and drives water turbines during peak demand hours. During low-demand hours, the same water is pumped back to the reservoir using the surplus electricity available at that time.

- TQ1.8 What are the advantages of three-phase a.c. systems?

- The advantages of three phase over a single phase system are: The amount of conductor material required is less for three phase system. Domestic power and industrial/commercial power can be provided from the same source for three phase system. Voltage regulation of a three phase system is better

- A polyphase system is a means of distributing alternating-current electrical power. ... Polyphase systems are particularly useful for transmitting power to electric motors. The most common example is the three-phase power system used for industrial applications and for power transmission

- TQ1.9 What is the main disadvantage of the original d.c. supply systems?

Disadvantages of DC (Compared to AC. When commercial use of

electricity became widespread, certain

disadvantages in using direct current in the home became

apparent. If a commercial direct current system is used, the

voltage must be generated at the level (amplitude or value)

required by the load. To properly light a 240 volt lamp, for

example, the dc generator must deliver 240 volts. If a 120 volt

lamp is to be supplied power from the 240 volt generator, a

resistor or another 120 volt lamp must be placed in series with

the 120 volt lamp to drop the extra 120 volts. When the

resistor is used to reduce the voltage, an amount of power equal

to that consumed by the lamp is wasted

Another disadvantage of the direct current system becomes

evident when the direct current (I) from the generating station

must be transmitted a long distance over wire to The consumer.

When this happens, a large amount of power is lost due to the

resistance (R) of the wire.

- TQ1.10 Describe the principles and advantages of modern d.c. transmission.

- The Advantages of DC. More efficient: Over long distances, DC transmission can move more power with less electrical losses than an equivalent AC transmission line. Lower Cost: Higher efficiency means a lower transmission cost, helping renewable energy compete against other power sources

- TQ1.11. What role do substations play in the transmission and distribution of electricity?

- To step up the generator level to transmission level voltage at the start of transmission lines and to step down the voltage at the end of the line to utilization voltage level.

- TQ1.12 Explain the function of the fourth conductor in the three-phase low-voltage distribution system.

A four-wire system allows to have phase voltages or line to ground voltages. Also it has the possibility of a grounded system, but, also you have zero sequence currents flowing through the neutral conductor if the system is feeding an unbalanced (possible on a fault) or harmonic (3th or its odd multiples) load.

The 4th wire is not for grounding. It's for return of current on unbalanced systems. The advantage of a 4 wire system is that when a fault occurs, there is more flexibility to keep the system running since it may only affect one of the phases.

Three phase four wire system can be used as single phase by utilizing one phase and neutral. But in three phase three wire there is no neutral.

- TQ1.13 With the aid of a diagram, briefly explain what a SWER system is and where it’s used

Single-wire earth return (SWER) or single-wire ground return is a single-wire transmission line which supplies single-phase electric power from an electrical grid to remote areas at low cost. Its distinguishing feature is that the earth (or sometimes a body of water) is used as the return path for the current, to avoid the need for a second wire (or neutral wire) to act as a return path.

Single-wire earth return is principally used for rural electrification, but also finds use for larger isolated loads such as water pumps. It is also used for high-voltage direct current over submarine power cables. Electric single-phase railway traction, such as light rail, uses a very similar system. It uses resistors to earth to reduce hazards from rail voltages, but the primary return currents are through the rails

SWER is a viable choice for a distribution system when conventional return current wiring would cost more than SWER’s isolation transformers and small power losses. Power engineers experienced with both SWER and conventional power lines rate SWER as equally safe, more reliable, less costly, but with slightly lower efficiency than conventional lines.[3] SWER can cause fires when maintenance is poor, and bushfire is a risk.[4]

Power is supplied to the SWER line by an isolating transformer of up to 300 kVA. This transformer isolates the grid from ground or earth, and changes the grid voltage (typically 22 or 33 kV line-to-line) to the SWER voltage (typically 12.7 or 19.1 kV line-to-earth).

The SWER line is a single conductor that may stretch for tens or even hundreds of kilometres, with a number of distribution transformers along its length. At each transformer, such as a customer's premises, current flows from the line, through the primary coil of a step-down isolation transformer, to earth through an earth stake. From the earth stake, the current eventually finds its way back to the main step-up transformer at the head of the line, completing the circuit.[3] SWER is therefore a practical example of a phantom loop.

In areas with high-resistance soil, the resistance of the soil wastes energy. Another issue is that the resistance may be high enough that insufficient current flows into the earth neutral, causing the grounding rod to float to higher voltages. Self-resetting circuit breakers usually reset because of a difference in voltage between line and neutral. Therefore, with dry, high-resistance soils, the reduced difference in voltage between line and neutral may prevent breakers from resetting. In Australia, locations with very dry soils need the grounding rods to be extra deep.[5] Experience in Alaska shows that SWER needs to be grounded below permafrost, which is high-resistance.[6]

The secondary winding of the local transformer will supply the customer with either single ended single phase (N-0) or split phase (N-0-N) power in the region’s standard appliance voltages, with the 0 volt line connected to a safety earth that does not normally carry an operating current.

A large SWER line may feed as many as 80 distribution transformers. The transformers are usually rated at 5 kVA, 10 kVA and 25 kVA. The load densities are usually below 0.5 kVA per kilometer (0.8 kVA per mile) of line. Any single customer’s maximum demand will typically be less than 3.5 kVA, but larger loads up to the capacity of the distribution transformer can also be supplied.

Some SWER systems in the USA are conventional distribution feeders that were built without a continuous neutral (some of which were obsoleted transmission lines that were refitted for rural distribution service). The substation feeding such lines has a grounding rod on each pole within the substation; then on each branch from the line, the span between the pole next to and the pole carrying the transformer would have a grounded conductor (giving each transformer two grounding points for safety reasons).