- An electrochemical cell which:

a)	can be recharged is termed a ________________cell

b)	cannot  b e recharged is termed a ________________cell.

Secondary/Primary

- Calculate the theoretical terminal voltage of a copper-aluminium cell.

______See TQ8.2.2 PDF __________

#### REFERENCE

#### How to measure the cell potential?

The image above is an electrochemical cell. The voltmeter at the very top in the gold color is what measures the cell voltage, or the amount of energy being produced by the electrodes. This reading from the voltmeter is called the voltage of the electrochemical cell. This can also be called the potential difference between the half cells, Ecell. Volts are the amount of energy for each electrical charge; 1V=1J/C: V= voltage, J=joules, C=coulomb. The voltage is basically what propels the electrons to move. If there is a high voltage, that means there is high movement of electrons. The voltmeter reads the transfer of electrons from the anode to the cathode in Joules per Coulomb.

### Cell Diagram

The image above is called the cell diagram. The cell diagram is a representation of the overall reaction in the electrochemical cell. The chemicals involved are what are actually reacting during the reduction and oxidation reactions. (The spectator ions are left out).  In the cell diagram, the anode half cell is always written on the left side of the diagram, and in the cathode half cell is always written on the right side of the diagram. Both the anode and cathode are seperated by two vertical lines (ll) as seen in the blue cloud above. The electrodes (yellow circles) of both the anode and cathode solutions are seperated by a single vertical line (l). When there are more chemicals involved in the aqueous solution, they are added to the diagram by adding a comma and then the chemical. For example, in the image above, if copper wasn't being oxidized alone, and another chemical like K was involved, you would denote it as (Cu, K) in the diagram. The cell diagram makes it easier to see what is being oxidized and what is being reduced. These are the reactions that create the cell potential.

### Standard Cell Potential

The standard cell potential (\(E^o_{cell}\)) is the difference of the two electrodes, which forms the voltage of that cell. To find the difference of the two half cells, the following equation is used:

\[E^o_{Cell}= E^o_{Red,Cathode} - E^o_{Red,Anode} \tag{1a}\]

with

- \(E^o_{Cell}\) is the standard cell potential (under 1M, 1 Barr and 298 K).

- \(E^o_{Red,Cathode}\) is the standard reduction potential for the reduction half reaction occurring at the cathode

- \(E^o_{Red,Anode}\) is the standard reduction potential for the oxidation half reaction occurring at the anode

The units of the potentials are typically measured in volts (V). Note that this equation can also be written as a sum rather than a difference

\[E^o_{Cell}= E^o_{Red,Cathode} + E^o_{Ox,Anode} \tag{1b}\]

where we have switched our strategy from taking the difference between two reduction potentials (which are traditionally what one finds in reference tables) to taking the sum of the oxidation potential and the reduction potential (which are the reactions that actually occur). Since E^o_{Red}=-E^o_{Ox}, the two approaches are equivalent.

#### Standard Cell Potential Example

The example will be using the picture of the Copper and Silver cell diagram. The oxidation half cell of the redox equation is:

Cu(s) → Cu2+(aq) + 2e- EoOx= -0.340 V

where we have negated the reduction potential EoRed= 0.340 V, which is the quantity we found from a list of standard reduction potentials, to find the oxidation potential EoOx. The reduction half cell is:

( Ag+ + e- → Ag(s) ) x2  EoRed= 0.800 V

where we have multiplied the reduction chemical equation by two in order to balance the electron count but we have not doubled EoRed since Eo values are given in units of voltage. Voltage is energy per charge, not energy per reaction, so it does not need to account for the number of reactions required to produce or consume the quantity of charge you are using to balance the equation. The chemical equations can be summed to find:

Cu(s) + 2Ag+ + 2e- → Cu2+(aq) + 2Ag(s) + 2e-

and simplified to find the overall reaction:

Cu(s) + 2Ag+ → Cu2+(aq) + 2Ag(s)

where the potentials of the half-cell reactions can be summed

EoCell= EoRed,Cathode+EoOx,Anode

EoCell = 0.800 V + (-0.340 V)

EoCell = 0.460V

to find that the standard cell potential of this cell is 0.460 V. We are done.

Note that since E^o_{Red}=-E^o_{Ox} we could have accomplished the same thing by taking the difference of the reduction potentials, where the absent or doubled negation accounts for the fact that the reverse of the reduction reaction is what actually occurs.

EoCell= EoRed,Cathode-EoRed,Anode

EoCell = 0.800V - 0.340V

EoCell = 0.460V

]

Electrolysis involves the manipulation of chemical reactions based on their electric potential. The reaction between the two elements in an electrolytic cell is a reduction-oxidation -- or redox -- reaction. The element that is reduced gains electrons, while element that is oxidized loses electrons. The nature of this reaction depends on the properties of the elements involved.

- Electric Potentials in Reactions

When elements gain or lose electrons, a change in electric potential results. This can be measured in electron volts. The reaction in an electrolytic cell is not spontaneous. In other words, it does not occur naturally. Instead, electrical energy must be applied to the system in order to create a reaction. This is different from a the reaction in a voltaic cell, which produces electrical energy. In such a case, the electric potential is positive. In an electrolytic cell, the electric potential is negative.

- Aluminum and Copper

In order to determine the behavior of aluminum and copper in an electrolytic cell, you must consider the potentials of each of the elements separately. The individual reductions or oxidations are called half-reactions. In the aluminum half-reaction, the aluminum ion has a charge of positive three. When it is reduced, it gains three electrons. The potential for this half-reaction is -1.66 electron volts. In the copper half-reaction, the copper ion has a charge of positive two. When it is reduced, it gains two electrons. The potential for this half-reaction is 0.34 electron volts. Two requirements of an electrolytic cell are that a redox reaction occur and that the potential be negative. If aluminum is oxidized, the potential is 1.66 electron volts. If copper is oxidized, the potential is -0.34 electron volts. Therefore, for a redox reaction with a negative potential, aluminum must be reduced and copper must be oxidized. The potential for this reaction is -2.00 electron volts.

- Cathode, Anode and Electrolyte

In electrochemical cells, the cathode is the site where reduction occurs. The anode is the site where oxidation occurs. Therefore, in an electrolytic cell of aluminum and copper, the aluminum would be reduced at the cathode, while the copper would be oxidized at the anode. A typical electrochemical cell has an ionic solution called an electrolyte. The exact nature of this solution can vary, but it should contain ions of both elements, often separated by a barrier. Ions from the solution will be reduced to solid aluminum at the cathode. At the anode, ions will form from the copper.

- Which electrode of the following pairs of electrodes would be the positive terminal?

a)	nickel-iron ________________

b)	nickel-cadmium ________________

[Source:  Ref R-8-A Section 12 Part A (Primary Cells), Activity 1, Q4, P259]

- The term given for hydrogen bubbles building up on the cathode of a cell is termed:

Electrolysis

[Source:  Ref R-8-A Section 12 Part A (Primary Cells), Activity 2, Q1, P263]

- The liquid that conducts between two electrodes in a cell is called

Electrolyte

[Source:  Ref R-8-A Section 12 Part A (Primary Cells) Activity 2, Q2, P264]

- Which of the following cells would you expect to have the longest shelf life?
(a)	carbon zinc cell
(b)	lithium cell
(c)	alkaline cell
(d)	mercury cell.

Answer: _______________________

alkalines should last between five and seven years, carbon zinc for three to five years, and lithium cells for 10 to 15 years on the shelf.D The open circuit voltage of a carbon zinc cell is:

________________

[Source:  Ref R-8-A Section 12 Part A (Primary Cells) Activity 3, Question 1, P273]

- The open circuit voltage of a lithium manganese cell is:

________________3.8V

[Source:  Ref R-8-A Section 12 Part A (Primary Cells) Activity 3, Q3, P273]

Nominal Cell Voltage (V)

- lithium cobalt oxide – 3.6

- lithium iron phosphate – 3.3

- lithium manganese oxide – 3.8

- What approximately is the open circuit terminal voltage for a lead acid cell:

________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Activity 1, Q1, P288]

Nominal Cell Voltage (V):			2.105

Capacity (Wh/kg):				60 to 75

Min/Max Operating Temperature (℃)	-40 to +60

- The specific gravity of a fully charged lead acid cell should be approximately:

________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Activity 1, Q4, P289]

By definition, the specific gravity of water is 1.00 and the specific gravity of the sulphuric acid electrolyte in a typical fully charged battery is 1.265-1.300.

- The gases produced by a lead acid cell towards the end of charge are:

________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Activity 1, Q5, P289]

What type of gas is released by a lead acid battery during charging?

hydrogen gas

The charging of lead-acid batteries can be hazardous. However, many workers may not see it that way since it is such a common activity in many workplaces. The two primary risks are from hydrogen gas formed when the battery is being charged and the sulfuric acid in the battery fluid.

- The open circuit terminal voltage for a nickel-cadmium cell is approximately:

________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Activity 2, Q1, P296]

Specific Energy (Wh/kg):		40 to 60

Nominal Cell Voltage (V)		1.2

Durability (Charge/Discharge cycles)	2000

Temperature Range (℃	):		 -40 to +60

- The specific gravity of an alkaline secondary cell should be around:

________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Activity 2, Q4, P296]

.3 Alkaline Cell ... secondary cells. The most common example of a secondary, or rechargeable cell, is the lead-acid automobile battery. ... Normally, the electrolyte for a battery is mixed such that the specific gravity is less than 1.350. Specific ...

### Specific Gravity

Specific gravity is defined as the ratio comparing the weight of any liquid to the weight of an equal volume of water. The specific gravity of pure water is 1.000. Lead-acid batteries use an electrolyte which contains sulfuric acid. Pure sulfuric acid has a specific gravity of 1.835, since it weighs 1.835 times as much as pure water per unit volume.

Since the electrolyte of a lead-acid battery consists of a mixture of water and sulfuric acid, the specific gravity of the electrolyte will fall between 1.000 and 1.835. Normally, the electrolyte for a battery is mixed such that the specific gravity is less than 1.350.

Specific gravity is measured with a hydrometer. A simple hydrometer consists of a glass float inside a glass tube, as shown in Figure 5. The hydrometer float is weighted at one end and sealed at both ends. A scale calibrated in specific gravity is positioned lengthwise along the body of the float. The float is placed inside the glass tube, and the fluid to be tested is drawn into the tube. As the fluid is drawn into the tube, the hydrometer float will sink to a certain level in the fluid. The extent to which the hydrometer float protrudes above the level of the fluid depends on the specific gravity of the fluid. The reading on the float scale at the surface of the fluid is the specific gravity of the fluid.

- The neutralising agent for acid based electrolytes is:

________________ What would you add to an acid to neutralize it?

Chemicals with a pH of 7 are considered neutral acids and typically have a pH less than 7. To neutralize them, use a weak base. There are two types of acids: mineral (inorganic) acids—such as sulfuric, hydrochloric, or nitric—and carboxylic (organic) acids such as formic or acetic. ... Use a weak acid to neutralize bases.Apr 2, 2009

A strong base is one that is fully dissociated in aqueous solution. For example, sodium hydroxide, NaOH, is a strong base. When a strong acid is neutralized by a strong base there are no excess hydrogen ions left in the solution. The solution is said to be neutral as it is neither acidic nor alkaline.

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Review Questions, Q8, P301]

- Explain why a sealed secondary cell could explode if it is subjected to overcharging.

____________________________________________________________________

____________________________________________________________________

[Source:  Ref R-8-A Section 12 Part B (Secondary Cells) Review Questions, Q15, P302]

Find out how to prolong battery life by using correct charge methods.

Charging and discharging batteries is a chemical reaction, but Li-ion is claimed to be the exception. Battery scientists talk about energies flowing in and out of the battery as part of ion movement between anode and cathode. This claim carries merits but if the scientists were totally right, then the battery would live forever. They blame capacity fade on ions getting trapped, but as with all battery systems, internal corrosion and other degenerative effects also known as parasitic reactions on the electrolyte and electrodes till play a role. (See BU-808b: What causes Li-ion to die?.)

The Li ion charger is a voltage-limiting device that has similarities to the lead acid system. The differences with Li-ion lie in a higher voltage per cell, tighter voltage tolerances and the absence of trickle or float charge at full charge. While lead acid offers some flexibility in terms of voltage cut off, manufacturers of Li-ion cells are very strict on the correct setting because Li-ion cannot accept overcharge. The so-called miracle charger that promises to prolong battery life and gain extra capacity with pulses and other gimmicks does not exist. Li-ion is a “clean” system and only takes what it can absorb.

## Charging Cobalt-blended Li-ion

Li-ion with the traditional cathode materials of cobalt, nickel, manganese and aluminum typically charge to 4.20V/cell. The tolerance is +/–50mV/cell. Some nickel-based varieties charge to 4.10V/cell; high capacity Li-ion may go to 4.30V/cell and higher. Boosting the voltage increases capacity, but going beyond specification stresses the battery and compromises safety. Protection circuits built into the pack do not allow exceeding the set voltage.

Figure 1 shows the voltage and current signature as lithium-ion passes through the stages for constant current and topping charge. Full charge is reached when the current decreases to between 3 and 5 percent of the Ah rating.

Figure 1: Charge stages of lithium-ion. Li-ion is fully charged when the current drops to a set level. In lieu of trickle charge, some chargers apply a topping charge when the voltage drops. Courtesy of Cadex

The advised charge rate of an Energy Cell is between 0.5C and 1C; the complete charge time is about 2–3 hours. Manufacturers of these cells recommend charging at 0.8C or less to prolong battery life; however, most Power Cells can take a higher charge C-rate with little stress. Charge efficiency is about 99 percent and the cell remains cool during charge.

Some Li-ion packs may experience a temperature rise of about 5ºC (9ºF) when reaching full charge. This could be due to the protection circuit and/or elevated internal resistance. Discontinue using the battery or charger if the temperature rises more than 10ºC (18ºF) under moderate charging speeds.

Full charge occurs when the battery reaches the voltage threshold and the current drops to 3 percent of the rated current. A battery is also considered fully charged if the current levels off and cannot go down further. Elevated self-discharge might be the cause of this condition.

Increasing the charge current does not hasten the full-charge state by much. Although the battery reaches the voltage peak quicker, the saturation charge will take longer accordingly. With higher current, Stage 1 is shorter but the saturation during Stage 2 will take longer. A high current charge will, however, quickly fill the battery to about 70 percent.

Li-ion does not need to be fully charged as is the case with lead acid, nor is it desirable to do so. In fact, it is better not to fully charge because a high voltage stresses the battery. Choosing a lower voltage threshold or eliminating the saturation charge altogether, prolongs battery life but this reduces the runtime. Chargers for consumer products go for maximum capacity and cannot be adjusted; extended service life is perceived less important.

Some lower-cost consumer chargers may use the simplified “charge-and-run” method that charges a lithium-ion battery in one hour or less without going to the Stage 2 saturation charge. “Ready” appears when the battery reaches the voltage threshold at Stage 1. State-of-charge (SoC) at this point is about 85 percent, a level that may be sufficient for many users.

Certain industrial chargers set the charge voltage threshold lower on purpose to prolong battery life. Table 2 illustrates the estimated capacities when charged to different voltage thresholds with and without saturation charge. (See also BU-808: How to Prolong Lithium-based Batteries.)

| Charge V/cell | Capacity at cut-off voltage* | Charge time | Capacity with full saturation |
| --- | --- | --- | --- |
| 3.80 3.90 4.00 4.10 4.20 | ~40% ~60% ~70% ~80% ~85% | 120 min 135 min 150 min 165 min 180 min | ~65% ~75% ~80% ~90% 100% |

Table 2: Typical charge characteristics of lithium-ion. Adding full saturation at the set voltage boosts the capacity by about 10 percent but adds stress due to high voltage.

* Readings may vary

When the battery is first put on charge, the voltage shoots up quickly. This behavior can be compared to lifting a weight with a rubber band, causing a lag. The capacity will eventually catch up when the battery is almost fully charged (Figure 3). This charge characteristic is typical of all batteries. The higher the charge current is, the larger the rubber-band effect will be. Cold temperatures or charging a cell with high internal resistance amplifies the effect.

Figure 3: Volts/capacity vs. time when charging lithium-ion. The capacity trails the charge voltage like lifting a heavy weight with a rubber band. Courtesy of Cadex

Estimating SoC by reading the voltage of a charging battery is impractical; measuring the open circuit voltage (OCV) after the battery has rested for a few hours is a better indicator. As with all batteries, temperature affects the OCV, so does the active material of Li-ion. SoC of smartphones, laptops and other devices is estimated by coulomb counting. (See BU-903: How to Measure State-of-charge.)

Li-ion cannot absorb overcharge. When fully charged, the charge current must be cut off. A continuous trickle charge would cause plating of metallic lithium and compromise safety. To minimize stress, keep the lithium-ion battery at the peak cut-off as short as possible.

Once the charge is terminated, the battery voltage begins to drop. This eases the voltage stress. Over time, the open circuit voltage will settle to between 3.70V and 3.90V/cell. Note that a Li-ion battery that has received a fully saturated charge will keep the voltage elevated for a longer than one that has not received a saturation charge.

When lithium-ion batteries must be left in the charger for operational readiness, some chargers apply a brief topping charge to compensate for the small self-discharge the battery and its protective circuit consume. The charger may kick in when the open circuit voltage drops to 4.05V/cell and turn off again at 4.20V/cell. Chargers made for operational readiness, or standby mode, often let the battery voltage drop to 4.00V/cell and recharge to only 4.05V/cell instead of the full 4.20V/cell. This reduces voltage-related stress and prolongs battery life.

Some portable devices sit in a charge cradle in the ON position. The current drawn through the device is called the parasitic load and can distort the charge cycle. Battery manufacturers advise against parasitic loads while charging because they induce mini-cycles. This cannot always be avoided and a laptop connected to the AC main is such a case. The battery might be charged to 4.20V/cell and then discharged by the device. The stress level on the battery is high because the cycles occur at the high-voltage threshold, often also at elevated temperature.

A portable device should be turned off during charge. This allows the battery to reach the set voltage threshold and current saturation point unhindered. A parasitic load confuses the charger by depressing the battery voltage and preventing the current in the saturation stage to drop low enough by drawing a leakage current. A battery may be fully charged, but the prevailing conditions will prompt a continued charge, causing stress.

## Charging Non-cobalt-blended Li-ion

While the traditional lithium-ion has a nominal cell voltage of 3.60V, Li-phosphate (LiFePO) makes an exception with a nominal cell voltage of 3.20V and charging to 3.65V. Relatively new is the Li-titanate (LTO) with a nominal cell voltage of 2.40V and charging to 2.85V. (See BU-205: Types of Lithium-ion.)

Chargers for these non cobalt-blended Li-ions are not compatible with regular 3.60-volt Li-ion. Provision must be made to identify the systems and provide the correct voltage charging. A 3.60-volt lithium battery in a charger designed for Li-phosphate would not receive sufficient charge; a Li-phosphate in a regular charger would cause overcharge.

## Overcharging Lithium-ion

Lithium-ion operates safely within the designated operating voltages; however, the battery becomes unstable if inadvertently charged to a higher than specified voltage. Prolonged charging above 4.30V on a Li-ion designed for 4.20V/cell will plate metallic lithium on the anode. The cathode material becomes an oxidizing agent, loses stability and produces carbon dioxide (CO2). The cell pressure rises and if the charge is allowed to continue, the current interrupt device (CID) responsible for cell safety disconnects at 1,000–1,380kPa (145–200psi). Should the pressure rise further, the safety membrane on some Li-ion bursts open at about 3,450kPa (500psi) and the cell might eventually vent with flame. (See BU-304b: Making Lithium-ion Safe.)

Venting with flame is connected with elevated temperature. A fully charged battery has a lower thermal runaway temperature and will vent sooner than one that is partially charged. All lithium-based batteries are safer at a lower charge, and this is why authorities will mandate air shipment of Li-ion at 30 percent state-of-charge rather than at full charge. (See BU-704a: Shipping Lithium-based Batteries by Air.).

The threshold for Li-cobalt at full charge is 130–150ºC (266–302ºF); nickel-manganese-cobalt (NMC) is 170–180ºC (338–356ºF) and Li-manganese is about 250ºC (482ºF). Li-phosphate enjoys similar and better temperature stabilities than manganese. (See also BU-304a: Safety Concerns with Li-ion and BU-304b: Making Lithium-ion Safe.)

Lithium-ion is not the only battery that poses a safety hazard if overcharged. Lead- and nickel-based batteries are also known to melt down and cause fire if improperly handled. Properly designed charging equipment is paramount for all battery systems and temperature sensing is a reliable watchman.

## Summary

Charging lithium-ion batteries is simpler than nickel-based systems. The charge circuit is straight forward; voltage and current limitations are easier to accommodate than analyzing complex voltage signatures, which change as the battery ages. The charge process can be intermittent, and Li-ion does not need saturation as is the case with lead acid. This offers a major advantage for renewable energy storage such as a solar panel and wind turbine, which cannot always fully charge the battery. The absence of trickle charge further simplifies the charger. Equalizing charger, as is required with lead acid, is not necessary with Li-ion.

Consumer and most industrial Li-ion chargers charge the battery fully. They do not offer adjustable end-of-charge voltages that would prolong the service life of Li-ion by lowering the end charge voltage and accepting a shorter runtime. Device manufacturers fear that such an option would complicate the charger. Exceptions are electric vehicles and satellites that avoid full charge to achieve long service life.

## Simple Guidelines for Charging Lithium-based Batteries

- Turn off the device or disconnect the load on charge to allow the current to drop unhindered during saturation. A parasitic load confuses the charger.

- Charge at a moderate temperature. Do not charge at freezing temperature. (See BU-410: Charging at High and Low Temperatures)

- Lithium-ion does not need to be fully charged; a partial charge is better.

- Not all chargers apply a full topping charge and the battery may not be fully charged when the “ready” signal appears; a 100 percent charge on a fuel gauge may be a lie.

- Discontinue using charger and/or battery if the battery gets excessively warm.

- Apply some charge to an empty battery before storing (40–50 percent SoC is ideal). (See BU-702: How to Store Batteries.)

- What is the variation in terminal voltage of a battery with load caused by?

____________________________________________________________________

[Source:  Ref R-8-A Section 13 Review Questions, Q4, P321]

What is meant by terminal voltage of a battery?

The electromotive force (emf) is the potential difference of a source when no current is flowing. Terminal voltage is the voltage output of a device is measured across its terminals. Terminal voltage is calculated by V = emf – Ir.

A battery with low internal resistance delivers high current on demand. High resistance causes the battery to heat up and the voltage to drop. ... Temperature also affects the resistance; heat lowers it and cold raises it. Heating the battery will momentarily lower the internal resistance to provide extra runtime.Feb 8, 2017

- Four 1.5 volt cells are connected in series, but one cell is reversed.  What is the net output voltage?

________________4.5V

[Source:  Ref R-8-A Section 13 Review Questions, Q5, P321]

- A 2 volt secondary cell with internal resistance of 0.05 ohm is connected to a load of 0.2 ohm. What is the current flowing through the load?

________________

E= 2 x 2 = 4V

R = 2 x 0.05 = 0.1 ohm

Rt= 0.2+0.1 = 0.3 ohm

4

I =------------------= 13.33A

0.3

[Source:  Ref R-8-A Section 13 Review Questions, Q10, P322]

- Calculate the continuous current that a battery with a 300 Ah rating can deliver on a 10 hour discharge

________________

[Source:  Ref R-8-A Section 13 Review Questions, Q11, P323]

AH                   300

I = ---------------= ----------------= 30A

Hr                     10

- Calculate the continuous current that the same battery in question TQ-8-2-19 can deliver if it is discharged in 5 hours if the Ah output is reduced to 80% of the 10 hour rating.

________________

[Source:  Ref R-8-A Section 13 Review Questions, Q12, P323]

300x 0.8 / 5 = 48A

- Determine the terminal voltage and circuit current of a battery consisting of 10 cells connected in series, if each cell has an open circuit emf of 2.0 volts and an internal resistance of 0.2 ohms, when a load with a resistance of 8 ohms is connected.

E = 10 x 2 = 20V

R = 0.2 x 10 = 2 ohm

Rt = 8+2 = 10ohm

E                          20

I = ----------------------= ---------------= 2A

Rt                         10

________________

[Source:  Ref R-8-A Section 13 Review Questions, Q13, P323]

- Determine the terminal voltage and circuit current of a battery consisting of 15 cells connected in parallel, if each cell has an open circuit emf 1.5 volts and an internal resistance of 0.3 ohms, when a load of 0.18 ohms is connected

________________

[Source:  Ref R-8-A Section 13 Review Questions, Q14, P323]

Do it yourself

- Determine the terminal voltage and circuit current of a battery consisting of 36 cells. The cells are to be connected in a series / parallel combination so that the open circuit voltage is 9 volts.  Each cell has an open circuit emf of 1.5 volts and an internal resistance of 0.3 ohms.  The connected load is 1.2 ohms

________________

[Source:  Ref R-8-A Section 13 Review Questions, Q15, P323]

Do it yourself

TUTORIAL

To answer questions TQ-8-3-1 to TQ-8-3-5, you may need to refer to Section 7.3 of Ref. R-8-D (AS/NZS 3000:2007 Wiring Rules)

- What are the recognised electricity generation systems?	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q1, P346]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

- Section 7.3 of AS/NZS 3000 covers the requirements for electricity generation systems connected to electrical installations.  In accordance with section 7.3 an electricity generation system may consist of the following:

  - Engine-driven generator set

  - Stand-alone power system (eg photovoltaic, wind turbine or mini-hydro turbine)

  - Grid-connected inverter system

  - Battery system

- What method of control is required by Ref. R-8-D and where should it be located?.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q2, P347]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

- Changeover Equipment for Non-Parallel Operation.  Figures 8.1 and 8.2 of Ref R-8-E show typical arrangements and are reproduced below:

- Neutral and earth conductors.  The switching of the generator neutral may be required to avoid multiple MEN connections. The normal supply neutral must not be switched. Correct sizing of the earth and neutral conductors for a permanently connected generator set is essential as these conductors form the loop that carries the earth fault currents.

8.4 Requirements For Stand-By Generator Synchronise Close Transfer Trip

- This sub-section of Ref R-8-E deals with “Generator Synchronise Close Transfer Trip (SCTT)” which allows transfer to generator supply without complete disconnection of the load.

8.5 Requirements For Generator Parallel Operation

- This clause covers the use of a generator for extended parallel operation.  Customers must provide a statement of the operating condition of the generator. This will specify that the generator may be run in parallel with the electricity distributor's supply system for extended periods as agreed with the electricity distributor. The customer must provide the electricity distributor with the following details of the equipment:

  - Site electrical drawings.

  - The protection settings of circuit breaker transfer switches and interlocking arrangements.

  - Earthing provisions.

  - The proposed installation date.

  - The size of the generator.

- Interconnection Protection.  The minimum interconnection protection requirements to allow parallel operation are:

  - Over and under voltage protection relays

  - Manually initiated, fully automatic synchronising equipment.

  - Overcurrent and earth fault protection.

  - A supervised battery supply for relays and tripping.

- Abnormal Operation Protection.  Devices must also be provided to protect the generator from abnormal operating conditions and shall include (as a minimum) protection against:

  - Reverse Power (Failure of Prime Mover).

  - Loss of Excitation (Pole Slipping).

  - Loss of Mains (Anti-lslanding).

- Further Protection.  Further protection may be installed as required by the generator manufacturer or consultant, for example:

  - Negative phase sequence.

  - Rotor earth fault.

  - Differential protection.

  - Thermal overload.

- Manual synchronisation is prohibited, unless monitored by a check synchronisation relay.

- Ref. R-8-D requires that electricity generation systems be provided with over current protection. Where should these devices be located in relation to the electricity generation system?.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q4, P347]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

- Protection Equipment.  Protection must consist of both active (anti-islanding) and passive systems.

- Active (Anti-islanding) Protection.  Active anti-islanding protection isolates the generation source from the distribution system in the event of a distribution system supply outage.  An example of this method is frequency drift. In this system the inverter is designed to lock to the distribution system frequency as a reference. The inverter frequency generator must then shift away from the nominal 50 Hz if the distribution system supply is not present, thereby, tripping the Over/Under frequency protection.

- Passive Protection. In addition to the above anti-islanding protection the customer's generation facilities must have the following minimum protection (in the inverter):

  - Over/under frequency.

  - Over/under voltage.

  - Over current and short circuit protection.

- What method of protective earthing should be used for Electricity Generation Systems?.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q6, P347]

__________________________________________________________________

__________________________________________________________________

Low impedance, High impedance, Compensated, Hybrid

See TQ83.4 Gen_Protection

- The diagram below shows connection of an alternative supply to a switchboard with a local MEN connection (three pole/four pole changeover).  Answer the questions shown on the diagram.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q9, P348]

1.	________________________________________________________________

2.	________________________________________________________________

3.	________________________________________________________________

4.	________________________________________________________________

5.	________________________________________________________________

6.	________________________________________________________________

7.	________________________________________________________________

8.	________________________________________________________________

9.	________________________________________________________________

1-3 ph Load 1

2-Change over switch

3-Generator load switch

4.Generator

5.

6.Neutral bar

7.Earth bar

8.Earthing point

9-3 ph Load 2

1.  Identify purpose of this line

2.  Identify purpose of these ‘switches’, what does the small triangle mean?

3.  Identify purpose of this ‘switch’?

4.  Identify  this

6.  Identify  this

7.  Identify  this

9.  Identify purpose of this line

8.  Identify  this

To answer questions TQ-8-3-6 to TQ-8-3-7, you may need to refer to Section 4.12 of Ref. R-8-D (AS/NZS 3000:2007 Wiring Rules)

- Define an electricity converter and give three examples of electricity converters. 	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q13/14, P350]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

A voltage converter is an electric power converter which changes the voltage of an electrical power source. It may be combined with other components to create a power supply.

- Where can an isolating switch be positioned in an electrical installation which is supplied through an electricity converter.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q15, P350]

__________________________________________________________________

__________________________________________________________________

Between converter and load

To answer questions TQ-8-3-8 to TQ-8-3-10 you may need to refer to Section 8 of R-8-E (Service and Installation Rules of New South Wales October 2006 As amended 4 July 2011)

- Section 8.6 of Ref. R-8-E outlines the requirements for the installation of private generation facilities on a customer’s premises that are connected to the grid. List the generation sources. 	[Source:  Ref R-8-A Section 14, Australian Standards and Local Requirements, Q18, P355]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

This clause outlines requirements for the installation of small scale generation facilities on a customer’s premises that are connected to the electricity distributor’s distribution system (grid) via an inverter. The generation source is most commonly solar photovoltaic (PV) arrays, but other sources are applicable.

- Who is responsible for the design installation and maintenance of generation facilities? 	[Source:  Ref R-8-A Section 14, Australian Standards and Local Requirements, Q19, P355]

__________________________________________________________________

Provider of Electricity Distribution

- Explain ‘Islanding’.	[Source:  Ref R-8-A Section 14 Australian Standards and Local Requirements, Q21, P355]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

Islanding. Islanding is the condition in which a distributed generator (DG) continues to power a location even though electrical grid power is no longer present. ... A common example of islanding is a distribution feeder that has solar panels attached to it.

- List four applications of a standby battery.	[Source:  Ref R-8-A Section 14 Exercise Questions, Q1, P369]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

- Standby power supplies are very essential components of many electrical systems and networks. They are required to provide continuous and secure service in the event of a power failure:

  - To bridge the initial gap between mains failure and the input from a generator.

  - To provide power to start a standby generator, automatically.

  - To provide full power, to allow for orderly shutdown of equipment

  - To provide lighting and power for a specified time.

  - To smooth transients in mains supply for voltage sensitive equipment.

- List three precautions which must be observed when charging a standby battery.	[Source:  Ref R-8-A Section 14 Exercise Questions, Q2, P369]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

- List three instances when a supplementary charge is to be applied to a standby battery.	[Source:  Ref R-8-A Section 14 Exercise Questions, Q4, P369]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

Precautions

- The following precautions should be taken when charging:

    - When a boost or supplementary charge has been completed the battery must be returned to the float condition to prevent damaging the cells.

    - Safety vent plugs fitted to cells must be firmly tight in place at all times during charging.

    - Electrolyte level must be maintained and electrolyte temperature should not be allowed to reach 45C.

    - Top up electrolyte level before charging if the charger voltage is limited to 2.4 Volts per cell (VPC), above this value top up towards the end of the recharge period.

    - Carry out a preventative maintenance schedule.

TUTORIAL

- Cite two advantages and two disadvantages of a central battery system (over a self contained system) to provide electrical power to egress lighting during times of mains power failure	[Source:  Notes]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

Central Battery System

- In this system supply to the evacuation lighting system is by a centralised battery bank. Fire rated cabling is run from the battery bank to supply light points throughout the building.

- Advantages of a centralised battery over self contained batteries are:

- One centralised battery provides for reduced maintenance time, by concentrating the battery source in the one space;

- In some installations, central systems can be less expensive to install

- Lights can be simple LED or compact fluorescent lamps;

- Batteries can be non specialised lead acid such as automotive units.

- Disadvantages of a centralised battery over self contained batteries are:

- All cabling between the battery and the luminaires must be fire rated. (MIMS, PVC in steel conduit, Radox, etc);

- Failure of the battery means total failure of the whole system;

- Sensing of circuit failure in isolated areas is very complex;

- A dedicated battery room is required which must be ventilated etc

- Give the definitions of “maintained mode”, “non-maintained mode” and “sustained maintained mode” of operation of emergency luminaires.	[Source:  Notes]

Maintained ________________________________________________________

__________________________________________________________________

Non maintained _____________________________________________________

__________________________________________________________________

Sustained  __________________________________________________________

__________________________________________________________________

Evacuation Luminaires:

- Evacuation luminaires are divided into 3 types:

Maintained

    - Lamp is operated normally by the supply, and continues to operate on battery supply should mains failure occur (see diagram below).

    - Until relatively recently maintained emergency luminaires usually consisted of 36, 18 or 9 Watt fluorescent lamps.  Now the trend is for compact fluorescent, LED and other energy saving lamps

During emergency the same lamp(s) are powered from rechargeable battery via an inverter, both the battery and inverter being contained within the luminaire. Wiring modifications include the provision of an un-switched active to maintain battery charging.

Emergency

Normal

Non Maintained

    - Luminaire is off during normal supply periods, actuating when supply fails and running from either self contained battery or central battery.

Lamps can be any of the energy efficient types

Normal

Emergency

Sustained

Two separate lamps are used, one for normal supply, and the other a separate unit for emergency supply.

Normal

Emergency

- Given an emergency luminaire with a photometric classification of C40.  Using Fig. F-8-4-1 determine the luminous intensity at an angle of 40 away from the vertical.	[Source:  Notes]

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

__________________________________________________________________

Emergency lighting is sometimes a confusing task, with a wide range of batteries and control gear on the market, not to mention different recommended ambient temperatures, test schedules and deciding if maintenance should be automatic or manual.

Here is where we come in! Below are a few things you should know when looking for an emergency fitting.

The two most important considerations when choosing an Emergency Luminaire are heat and light distribution. Testing is conducted through a series of rigorous hot and cold cycle testing with various time durations, ensuring that the minimum and maximum operating temperatures as well as run time of the battery pack fall within the allowable operating range. The minimum expected running time for emergency luminaires is 90 minutes, although through good design and correct choice of gear our emergency luminaire runs for 3 hours in emergency operation mode.

When designing our products, heat sinking is always top of mind, a factor that is incredibly important in ensuring the longevity of emergency batteries. When designing Emergency features into the extrusion, it is important to use the correct Emergency gear to match the ambient temperature ratings of the fittings to ensure the longevity of the battery.

Another consideration is clearance around the battery pack for air and heat transfer. Using materials such as aluminium; a natural heat sink, assists in making sure the battery temperature does not exceed its limit when placed inside an enclosed extrusion fitting

In addition to heat management, photometrics of the luminaire give an indication as to how many Emergency luminaires are required to meet emergency mode illuminance levels. Official NATA certified photometric testing provides us with a classification determining the maximum spacing at various mounting heights for the fitting using tables 5.1-5.5 (AS 2293.1-2005), in the C0 and C90 planes.

In normal operation, a luminaire with an emergency system integrated will function as per usual, while keeping the emergency battery charged. When emergency mode is triggered, the LED board connected to the battery will continue to be powered, until the battery is exhausted. It is a requirement to test the system at no greater than 6 month intervals, carried out in accordance with AS 2293.2.

- What is the minimum required illumination in general areas under mains failure conditions?.	[Source:  Notes]

__________________________________________________________________

Specific Locations

- Emergency escape luminaires are required:

  - within 2m of the approach side of each doorway requiring an exit sign:

  - within 2m of the intersection of the centre-lines of intersecting corridors.

  - within 2m of the intersection of centre-lines at each change of direction (other than on a staircase).

  - within 2m of any change of floor level, on the low' side.

You are required to design the layout of the emergency lighting system for a large open workshop measuring 80m x 40m with an effective ceiling height of 4.5m. The type of luminaire selected has a photometric classification of E10.  Using Fig. F-8-4-2 sketch the emergency luminaire layout for the workshop.	[Source:  Notes

Design work—Do it yourself

TUTORIAL

To answer the following questions you may need to consult AS/NZS 3000:2007

- Which code of practice will provide information regarding the location and number of smoke detectors in a domestic residence?

__________________________________________________________________

__________________________________________________________________

4.6 SMOKE ALARMS

National building codes and state legislation have requirements for

installation of smoke alarms including location, number required and

interconnection for alarm purposes.

Where mains-powered smoke alarms are fitted, such alarms may be

directly connected to the lighting final subcircuit or to an individual final

subcircuit.

- Smoke detectors may be connected in two circuit configurations. They are?

__________________________________________________________________

__________________________________________________________________

Ionisation Smoke Detector

- An ionisation chamber containing a minute amount of radioactive material (Americium).  Under normal conditions the air contained in the ionisation chamber is ionised and becomes conductive allowing a small current to flow from the battery through the chamber, through the detection circuit and back to the battery.  When smoke enters the chamber it disrupts the current flow and activates an alarm.  See Fig F-8-5-1 for principle of operation.  Ionization smoke detection is generally more responsive to flaming fires.

Fig F-8-5-1 Principle of Operation of an ionisation type detector

Photoelectric Smoke Detector

- Photoelectric smoke detectors use the principle of scattered or reflected light to indicate the presence of visual smoke. In the absence of smoke, the chamber is dark and light shines across the chamber and is received in a light trap on the far side. When smoke is present in the chamber, a photocell located at right angles to the light source senses the light scattered off the smoke particles and, at a certain level of illumination, triggers the alarm.  See Fig F-8-5-2 for principle of operation. Photoelectric smoke detection is generally more responsive to fires that begin with a long period of smouldering.

Heat Detector

- Two types are available:

  - Fixed Temperature Detector A fixed temperature detector measures the air temperature surrounding it and is the most common type of heat detector. For electrically connected heat detectors, the most common fixed temperature can be around 58°C. However, with technological developments, detectors have been enabled to activate at a temperature as low as 47°C thus increasing the available reaction time and margin of safety.

  - Rate-of-Rise Detector. A rate-of-rise detector monitors changes in temperature, for example an explosion. This type of heat detector is able to operate at a lower temperature  than a fixed temperature detector.

Fig F-8-5-2 Principle of Operation of a Photoelectric type detector

Fig F-8-5-3 Typical optical type smoke detector

- Why are smoke alarms connected to lighting circuits?

__________________________________________________________________

__________________________________________________________________

4.6 SMOKE ALARMS

National building codes and state legislation have requirements for

installation of smoke alarms including location, number required and

interconnection for alarm purposes.

Where mains-powered smoke alarms are fitted, such alarms may be

directly connected to the lighting final subcircuit or to an individual final

subcircuit.

NOTES:

1 Use of the lighting final subcircuit provides indication that the mains power

supply is available, as a loss of supply to smoke alarms in an electrical

installation would be indicated by the non-operation of lighting.

2 Smoke alarms are not considered to be safety services for the purposes of

this Standard.

- Are smoke alarms considered to be 'safety devices'?

__________________________________________________________________

__________________________________________________________________

Smoke alarms are not considered to be safety services for the purposes of

this Standard

- Is a separate main switch connected to the supply side of the general installation main switch required?

__________________________________________________________________

__________________________________________________________________

NSW Electrical Service Rule

8.6.10 Switching Requirements

The following installation main switches must be of the lockable or sealable form for safe isolation:

(a) The installation main switch(s) on the main switchboard.

(b) The generator supply main switch, refer to clause 8.6.19 Generator Supply Main Switch.

clause 8.6.19

The generator supply main isolating switch must be located on the switchboard at which the generation source is connected

- Is the use of fire rated cable mandatory of the circuit wiring?

__________________________________________________________________

__________________________________________________________________

Fire Resistant cables are used, where required by local fire codes, in the wiring of :

_ Fire resistant safety circuits

_ Public address and emergency voice communication systems in high-rise buildings

_ Control and instrumentation services in industrial, commercial and residential complexes

_ High-temperature installation conditions