- A cable or wiring system suitable for installation in a concrete slab would be:

[Source: Ref R-6-A, Section 3, Tutorial Question 1, P107]

  - Unenclosed TPI cable

  - Bare MIMS cable

  - TPI cable enclosed in rigid PVC conduit

  - Unenclosed TPS cable

- A suitable wiring system used as sub-mains to a site shed on a construction site is:

[Source: Ref R-6-A, Section 3, Tutorial Question 2, P106]

  - Thermoplastic sheathed cables with Catenary.

  - Flexible insulated conductors.

  - Polymeric insulated cable

  - Annealed copper conductors

- A suitable wiring system used to supply machinery on a factory production line is;

[Source: Ref R-6-A, Section 3, Tutorial Question 3, P106]

  - Thermoplastic sheathed cables with catenary.

  - Busbar trunking (busway)

  - MIMS cables on a cable tray

  - TPI conductors in medium duty conduit.

- A suitable wiring system used as aerial cable without further support is:

[Source: Ref R-6-A, Section 3, Tutorial Question 4, P106]

  - Thermoplastic sheathed cables

  - Flexible insulated conductors

  - Polymeric insulated cable

  - Annealed copper conductors

- A suitable wiring system for supply to a lift is:

[Source: Ref R-6-A, Section 3, Tutorial Question 5, P106]

  - V90 SDI cables on cable tray

  - V75 TPI cables in PVC rigid conduct

  - MIMS cables on a cable tray

  - TPS cables sharing the same conduit as power and light circuits.

- A suitable wiring system for smoke detectors connected to a fire indicator panel is:

[Source: Ref R-6-A, Section 3, Tutorial Question 6, P107]

  - TPS cable

  - TPI in steel conduit

  - Radox cable

  - XLPE on cable tray

- A suitable wiring system for sub-main in a factory is:

[Source: Ref R-6-A, Section 3, Tutorial Question 7, P107]

  - TPS cable

  - TPI in steel conduit

  - Radox cable

  - XLPE on cable tray

- A suitable wiring system for light fitting in suspended ceiling of a shopping centre is:

[Source: Ref R-6-A, Section 3, Tutorial Question 8, P107]

  - TPS cable

  - TPI in steel conduit

  - Radox cable

  - XLPE on cable tray.

- A suitable wiring system for vandal proof light fitting in bus shelter is:

[Source: Ref R-6-A, Section 3, Tutorial Question 9, P107]

  - TPS cable

- A suitable wiring system for a sub-main to a detached garage in a domestic installation is:

[Source: Ref R-6-A, Section 3, Tutorial Question 10, P107]

  - TPS cable.

  - TPI in steel conduit.

  - TPI in heavy duty conduit.

  - TPI suspended on a Catenary.

  - Radox cable

  - XLPE on cable tray

- A suitable and cost effective wiring system for irrigation pump on a rural property is:

[Source: Ref R-6-A, Section 3, Tutorial Question 11, P108]

  - Aluminium aerials

  - TPI in steel conduit.

  - TPI in heavy duty conduit.

  - 4 core + earth XLPE orange circular buried direct.

- What is the minimum depth of cover of a Category A underground wiring system, external to a building, below natural ground:

[Source: Ref R-6-A, Section 3, Tutorial Question 12, P108]

  - 300mm

  - 500mm

  - 600 mm

  - Not permitted

- A TPS wiring system installed within a PVC conduit in a concrete floor on, or above the ground would be deemed to have the same current carrying capacity as cables installed:

[Source: Ref R-6-A, Section 3, Tutorial Question 13, P108]

  - Enclosed in air

  - Buried direct in the ground

  - Unenclosed in air

- Cables enclosed in heavy-duty conduit, and chased into rock to a depth of not less than 50 mm, fall into the underground wiring system category of:

[Source: Ref R-6-A, Section 3, Tutorial Question 14, P108]

  - Category A

  - Category B

  - Category C

  - Not permitted as underground wiring.

- 3.11.3.3 Category C underground wiring system

- Category C underground wiring systems recognized by this Standard

- comprise cables chased in rock and covered with concrete.

- When single-insulated wire is installed in trunking or toughing that has a removable lid:

[Source: Ref R-6-A, Section 3, Tutorial Question 15, P108]

  - the cables must be taped together and held in position

  - the lid must be held in position with cable ties

  - building wire is not permitted in a duct which has a lid

  - the lid shall not be removed without a special tool if the duct is readily accessible

- The minimum height above ground for insulated live aerial conductors over a roadway is:

[Source: Ref R-6-A, Section 3, Tutorial Question 16, P109]

  - 3.0m

  - 4.6 m

  - 5.5m

- Insulated conductors are not permitted over a roadway

- Mineral insulated metal sheathed (MIMS) cables, which are buried in the ground without further enclosure, must be:

[Source: Ref R-6-A, Section 3, Tutorial Question 17, P109]

  - protected by a suitable serving

  - classed as a category A wiring system

  - protected by a type ‘D’ circuit breaker

  - buried at a depth of not less than 0.75 metre.

- The maximum current rating for a HRC fuse protecting a circuit with a maximum demand of 20 A and wired with a cable rated at 28 A would be:

[Source: Ref R-6-A, Section 3, Tutorial Question 19, P109]

  - 18A.

  - 20 A.

  - 25 A.

  - 28 A.

- A wiring system for a safety service has a WS classification of WS52. This means the wiring system can maintain its integrity under fire conditions for;

[Source: Ref R-6-A, Section 3, Tutorial Question 22, P110]

  - 52 minutes.

  - 60 minutes.

  - 5 hours.

  - 120 minutes.

- The maximum permitted operating temperature of a V90 insulated conductor in normal use is:

[Source: Ref R-6-A, Section 3, Tutorial Question 24, P110]

  - 90○ C

  - 75○ C

  - 40○ C

  - 25○ C

- Do it yourself tutorial 6.2

- Do it yourself tutorial 6.3

- TQ 6.43 The voltage drop between the point of supply a low voltage electrical installation and any point in that electrical installation must not exceed ______ of the nominal voltage at the point of supply;

[Source: Ref R-6-A, Section 7, Tutorial Q5, P219]

  - 2%

  - 5%

  - 7%

  - 10%

- TQ6.44 An acceptable line voltage drop across an entire 400V installation would be;

[Source: Ref R-6-A, Section 7, Tutorial Q7, P220]

  - 15V

  - 21V

  - 30V

  - 40V

- TQ6.45 Where the point of supply is the low voltage terminals of a substation located on the premises containing the electrical installation and dedicated to the installation, the permissible voltage drop may be;

[Source: Ref R-6-A, Section 7, Tutorial Q8, P220]

  - 2%

  - 5%

  - 7%

  - 10%

- The drop in voltage at any point in an extra-low voltage electrical installation shall not exceed ______ of the nominal value when all live conductors are carrying the circuit-operating current. [Source: Ref R-6-A, Section 7, Tutorial Q9, P220]

  - 2%

  - 5%

  - 7%

  - 10%

- Refer

### Example - Cable Selection Based on Voltage Drop

For the installation below:

- Calculate the maximum permissible voltage drop (VP) for the f.s.c.

- Calculate the maximum permissible value of Vc

- Determine the minimum cable size

#### Solution:

- Assuming 400/230V supply, the total allowable voltage drop between the point of supply and the load is 5% of 400V, i.e. 20V

As the consumer mains has a 12V drop the FSC allowable volt drop is 8V

- Vc=1000VdL×I=1000×830×32=8.333mV/A.mThen:

- Minimum cable size from Table 42 is 6 mm2

- To do TQ 6.48 to 6.52

- AS3008 Table 35

## Calculating Cable A.C. Resistance (RC)

### Example X-6-5-1: Determining RC from Tables

Calculate the A.C. resistance of a single conductor in a 45m length of 10 mm2, 4 Core and Earth  (4C + E) V90 Copper (Cu) cable.

#### Solution:

From Ref R-6-D, Table 35, Column 5, for 10 mm2 cable RC = 2.33 /km

R=RC×L1000=2.33×451000=0.105Ωand

## Tutorial 6.5

- The internal earth fault loop path is from;

[Source: Ref R-6-A, Section 8, Tutorial Q1, P249]

  - active to neutral conductor

  - active to phase conductor

  - active to protective earthing conductor

  - phase to functional earthing conductor.

- The external earth fault loop path is from;

[Source: Ref R-6-A, Section 8, Tutorial Q2, P249]

  - active to neutral conductor

  - active to phase conductor

  - active to protective earthing conductor

  - phase to functional earthing conductor.

- The maximum permissible disconnection time to provide fault protection (protection against indirect contact), for a circuit supplying 10A socket outlets is;

[Source: Ref R-6-A, Section 8, Tutorial Q3, P249]

  - 0.4 seconds

  - 1.45 seconds

  - 5 seconds

  - 1 hour

- The device that will operate to provide fault protection (protection against indirect contact) in the shortest time on a circuit supplying 10A socket outlets is;

[Source: Ref R-6-A, Section 8, Tutorial Q4, P249]

  - a H.R.C. fuse

  - an R.C.D.

  - a thermal magnetic circuit breaker

  - a thermal overload.

- The maximum permissible disconnection time to provide fault protection (protection against indirect contact), supplying lighting points, is;

[Source: Ref R-6-A, Section 8, Tutorial Q5, P249]

  - 0.4 seconds

  - 1.45 seconds

  - 5 seconds

  - 1 hour

## Earth Fault-loop and Disconnection Times

Emmy Kerrigan - Thursday, February 14, 2013

When questions arise regarding earth fault-loop and disconnection times for various equipment, refer to Section 5.7.2 in your AS 3000.

In general, GPOs have 0.4 second disconnection time. Others, like light circuits or directly connected equipment, have 5 second disconnection time. This is obviously dependent on the RCD and the impedance of the earthing system, as well as installation conditions such as wet locations, etc.

Correct earth loop impedance ensures the disconnection times stated in Section 5.7.2. However, the note in Section 5.7.5 suggests a 30mA RCD that will trip the circuit in 0.4sec may be used to satisfy the requirement.

Note that earth continuity is a different test. Earth continuity still has to be done as per Section 8.3.3 in AS3000.

Review your copy of the AS 3000:2007 Electrical Installations (Aus-NZ Wiring Rules), or check out these extracts:

## 5.7.2 Disconnection Times

The maximum disconnection time for a 230 V supply voltage shall not exceed the following:
   (a) 0.4 s for final subcircuits that supply—
        (i) socket-outlets having rated currents not exceeding 63 A; or
        (ii) hand-held Class I equipment; or
        (iii) portable equipment intended for manual movement during use.
   (b) 5 s for other circuits where it can be shown that people are not exposed to touch voltages that exceed safe values.

NOTES:
   1 Maximum disconnection times will vary for other operating voltages or installation conditions, such as wet locations, etc.
   2 The fault current must be of sufficient magnitude to cause automatic disconnection within the required times.

## 5.7.5 Note on other measures

Supplementary equipotential bonding
In the event that a reduction in earth fault-loop impedance is required in order to ensure that the disconnection time of the protective device is sufficient to satisfy the requirements of Clause 5.7.2, bonding of extraneous conductive parts and their connection to the earthing system may be used.

NOTE: Other measures, such as selection of an alternative protective device, e.g. an RCD that has a lower automatic operating current, Ia, within the required disconnection time may also be used to satisfy the requirements of Clause 5.7.2.

## 8.3.3 Mandatory Tests

The following tests shall be carried out on low voltage electrical installations:
   (a) Continuity of the earthing system (earth resistance of the main earthing conductor, protective earthing conductors and bonding conductors), in accordance with Clause 8.3.5.
   (b) Insulation resistance, in accordance with Clause 8.3.6.
   (c) Polarity, in accordance with Clause 8.3.7.
   (d) Correct circuit connections, in accordance with Clause 8.3.8.
   (e) Verification of impedance required for automatic disconnection of supply (earth fault-loop impedance), in accordance with Clause 8.3.9.
   (f) Operation of RCDs, in accordance with Clause 8.3.10.
If the electrical installation fails a test, that test and any preceding tests that may have been influenced by the fault indicated shall be repeated after the fault has been rectified.

NOTES:
   1 Item (e) above may require that supply is available.
   2 Item (f) above requires that supply is available.
   3 High voltage installations may require additional tests (see AS 2067 in Australia or the New Zealand Electricity Regulations in New Zealand).

- The device that will operate to provide fault protection (protection against indirect contact) in the shortest time on a circuit supplying lighting points is;

[Source: Ref R-6-A, Section 8, Tutorial Q6, P250]

  - a H.R.C. fuse.

  - an R.C.D.

  - a thermal magnetic circuit breaker

  - a thermal overload.

## Protection against indirect contact

By automatic disconnection of the circuit – The Standard IEC 60364 prescribes automatic disconnection of the supply for protection against indirect contact.

<img class="size-full wp-image-70264" src="https://electrical-engineering-portal.com/wp-content/uploads/2015/05/protection-indirect-contact-earth-fault.jpg" alt="Distribution systems and protection against indirect contact and earth fault – ABB" width="728" height="518" srcset="https://electrical-engineering-portal.com/wp-content/uploads/2015/05/protection-indirect-contact-earth-fault.jpg 728w, https://electrical-engineering-portal.com/wp-content/uploads/2015/05/protection-indirect-contact-earth-fault-120x85.jpg 120w, https://electrical-engineering-portal.com/wp-content/uploads/2015/05/protection-indirect-contact-earth-fault-280x199.jpg 280w" sizes="(max-width: 728px) 100vw, 728px" />Distribution systems and protection against indirect contact and earth fault – ABB

The protective device shall automatically disconnect the supply so that, in the event of a fault between a live part and an exposed-conductive-part or a protective conductor, a prospective touch voltage exceeding 50 V a.c. (25 V in special environments) does not persist for a time sufficient to cause a risk of harmful physiological effect in a person in contact with simultaneously acces- sible conductive parts.

This protective measure requires co-ordination between the connection to earth of the system and the characteristics of the protective conductors and devices.

The devices suitable for the automatic disconnection of the supply and able to detect earth fault currents are:

- Automatic circuit-breakers with thermomagnetic release;

- Automatic circuit-breakers with microprocessor-based electronic relay;

- Automatic circuit-breakers with microprocessor-based electronic relay with integrated protection against earth fault (function G);

- Thermal magnetic or electronic circuit-breakers with integrated residual current releases;

- Pure residual current circuit-breakers;

- Residual current releases.

- The maximum permissible disconnection time to provide fault protection (protection against indirect contact), for a sub-main rated at 63A, is;

[Source: Ref R-6-A, Section 8, Tutorial Q7, P250]

  - 0.4 seconds

  - 1.45 seconds

  - 5 seconds

  - 1 hour

- The device that should not be used to provide fault protection, for a sub-main rated at 63A, is;

[Source: Ref R-6-A, Section 8, Tutorial Q8, P250]

  - a H.R.C. fuse.

  - an R.C.D.

  - a thermal magnetic circuit breaker

  - an electronic circuit breaker

- When calculating the internal earth fault loop impedance the voltage present at the circuit protection device (reference point) is;

[Source: Ref R-6-A, Section 8, Tutorial Q9, P250]

  - 230V

  - 240V

  - 184V

  - 400V

- The maximum value of earth fault loop impedance for a sub main protected by a 63 A H.R.C. fuse is;

[Source: Ref R-6-A, Section 8, Tutorial Q10, P250]

  - 0.55Ω

  - 0.94Ω

  - 1.53Ω

  - 1MΩ.

- Earth fault loop impedance

NECA Technical have been receiving calls from members about readings obtained in relation to earth fault loop impedance from Network Operator Inspectors. In response to queries we have developed an "Earth Fault Loop Impedance" calculator which may assist in scenarios faced.

It should be understood that the reading obtained relates to the applied nominal voltage. Table 8.1 from the Wiring Rules (AS/NZS 3000:2007) Section 8 uses 230 volts as the applied nominal voltage.

TABLE 8.1

MAXIMUM VALUES OF EARTH

FAULT-LOOP IMPEDANCE (Zs at 230 V)

The formula used to populate this table is:

For example, relating to table 8.1 of the Wiring Rules the formula for a 230 volt supply, protected by a 63 amp Type C circuit breaker is:

230 volts divided by 63 amps (Protective device)  x 7.5 (Type C rated current)

We have broken this down into 4 steps for simplicity:

1.

2.

3.

4.

What does this mean?

In the above example we are using 230 volts, although normally you are on a network supplying around 245 volts. Applying the same formula using 245 volts and the same protective device looks like this:

NECA Technical will be making available a fact sheet on this subject. Access our Technical Knowledge Base (TKB) to learn more.

Tutorial questions TQ.6.32 to TQ.6.34 refer to following diagram:

- Calculate the total earth fault loop impedance for a circuit supplying a hot water system protected by a Clipsal 20A type ‘C’ circuit breaker.

[Source: Ref R-6-A, Section 8, Tutorial Q11, P251]

0.002 ohm

- Calculate the internal earth fault loop impedance for a circuit supplying a hot water system protected by a Clipsal 20A type ‘C’ circuit breaker.

[Source: Ref R-6-A, Section 8, Tutorial Q12, P251]

Zint = 0.8 Zs = 0.8 x 0.002 = 0.0016 ohm

- Example X-6-5-5: Earth fault loop impedance

Calculate the maximum permissible earth fault loop impedance (Zint) of a circuit supplying a hot water service type ‘C’ 20A M.C.B. in a 230/400 volt installation.

If this circuit is wired in 2.5 mm2 2C+E V90 orange circular cable and the length of the cable run is 60m.

- Determine the impedance of the cable between active and protective earthing conductors

- Does the circuit comply with AS 3000 requirement for earth fault loop impedance (Y/N) and why?

- Calculate the voltage drop on this section of cable.

#### Solution:

Zint=0.8U0Ia=0.8×2307.5×20=1.227Ω

- Active and Protective earthing conductor impedance

2.5mm2 Rc = 9.45Ω/km (AS3008.1 Table 35 Col 4) assume 90C

R =Rc1000 x  L  x 2 =9.451000 x 60 x 2 =1.134Ω

- Yes less than 1.227Ω (from question part (a))

- VC = 16.4 x 1.155 = 18.942mV/A.m (T42C8)

Vd=L x I x Vc1000=60 x 20 x  18.9421000=  22.73V

Type B circuit breaker Ia = 4 x rated current of circuit breaker

Type C circuit breaker Ia = 7.5 x rated current of circuit breaker

Type D circuit breaker Ia = 12.5 x rated current of circuit breaker

- If the hot water system of question TQ.6.33 is wired in 2.5mm2 Twin and Earth with a circuit length of 35 m;

[Source: Ref R-6-A, Section 8, Tutorial Q13, P252]

  - Calculate the internal earth fault loop impedance of the final sub-circuit (hint use AS3008.1.1 to determine Zph and Zpe)

  - Does the calculated internal earth loop impedance comply with AS3000?

  - Calculate the voltage drop on the H.W.S. final sub-circuit.

  - If 4.6V was lost on the consumers mains, does the final-sub circuit comply with AS3000 requirement for voltage drop? Y/N

- A 50 mm2 copper sub-main is protected by a 125A H.R.C. fuse with a route length of 80 m

[Source: Ref R-6-A, Section 8, Tutorial Q14, P252]

  - Determine from table 8.1 AS3000 the maximum permissible internal earth fault loop impedance.

  - Use table B1 of AS3000 to determine if the route length is compliant.

  - 0.2 ohm

- 50 sqmm -------- for fuse is 71 m   Now   80 m  Non compliance