- TQ3.1- Calculate the touch voltage for a single-phase final sub-circuit having 4.0mm2 active conductor having a per unit impedance of 1.0 and a 2.5mm2 earthing conductor having a per unit impedance of 2.4 where the operating voltage of the installation is 230V.

See the attached sheet

TQ3.2- List 4 methods of protect against direct contact

- Protection by the insulation of live parts

- Protection by means of barriers or enclosures

- Protection by means of obstacles, or by placing out of arm’s reach.

- Protection by use of Extra-Low Voltage (ELV) or by limitation of the energy of discharge.

- TQ3.3 What degree of protection is needed where barriers provide the method for protecting against direct contact with live parts?

- IP Coding  Refer TQ3.2-Enclouure and degree of protection

- For a 240-volt final subcircuit supplying fixed equipment or submain, what is the maximum disconnection time for automatic disconnection devices?

- Earth Fault-loop and Disconnection Times

Emmy Kerrigan - Thursday, February 14, 2013

When questions arise regarding earth fault-loop and disconnection times for various equipment, refer to Section 5.7.2 in your AS 3000.

In general, GPOs have 0.4 second disconnection time. Others, like light circuits or directly connected equipment, have 5 second disconnection time. This is obviously dependent on the RCD and the impedance of the earthing system, as well as installation conditions such as wet locations, etc.

Correct earth loop impedance ensures the disconnection times stated in Section 5.7.2. However, the note in Section 5.7.5 suggests a 30mA RCD that will trip the circuit in 0.4sec may be used to satisfy the requirement.

Note that earth continuity is a different test. Earth continuity still has to be done as per Section 8.3.3 in AS3000.

Review your copy of the AS 3000:2007 Electrical Installations (Aus-NZ Wiring Rules), or check out these extracts:

- 5.7.2 Disconnection Times

The maximum disconnection time for a 230 V supply voltage shall not exceed the following:
   (a) 0.4 s for final subcircuits that supply—
        (i) socket-outlets having rated currents not exceeding 63 A; or
        (ii) hand-held Class I equipment; or
        (iii) portable equipment intended for manual movement during use.
   (b) 5 s for other circuits where it can be shown that people are not exposed to touch voltages that exceed safe values.

NOTES:
   1 Maximum disconnection times will vary for other operating voltages or installation conditions, such as wet locations, etc.
   2 The fault current must be of sufficient magnitude to cause automatic disconnection within the required times.

- 5.7.5 Note on other measures

Supplementary equipotential bonding
In the event that a reduction in earth fault-loop impedance is required in order to ensure that the disconnection time of the protective device is sufficient to satisfy the requirements of Clause 5.7.2, bonding of extraneous conductive parts and their connection to the earthing system may be used.

NOTE: Other measures, such as selection of an alternative protective device, e.g. an RCD that has a lower automatic operating current, Ia, within the required disconnection time may also be used to satisfy the requirements of Clause 5.7.2.

- 8.3.3 Mandatory Tests

The following tests shall be carried out on low voltage electrical installations:
   (a) Continuity of the earthing system (earth resistance of the main earthing conductor, protective earthing conductors and bonding conductors), in accordance with Clause 8.3.5.
   (b) Insulation resistance, in accordance with Clause 8.3.6.
   (c) Polarity, in accordance with Clause 8.3.7.
   (d) Correct circuit connections, in accordance with Clause 8.3.8.
   (e) Verification of impedance required for automatic disconnection of supply (earth fault-loop impedance), in accordance with Clause 8.3.9.
   (f) Operation of RCDs, in accordance with Clause 8.3.10.
If the electrical installation fails a test, that test and any preceding tests that may have been influenced by the fault indicated shall be repeated after the fault has been rectified.

NOTES:
   1 Item (e) above may require that supply is available.
   2 Item (f) above requires that supply is available.
   3 High voltage installations may require additional tests (see AS 2067 in Australia or the New Zealand Electricity Regulations in New Zealand).

- TQ3.5 What means are suitable for providing protection from the risk of ignition of flammable materials in normal service?

Examples of separation include the following:

• distancing the dangerous goods from people, other dangerous goods or

protected works, pipelines, and other property, such that interaction is

not possible

• decanting in a fume cupboard to control emissions

• storing incompatible dangerous goods in separate buildings; separated

by a sufficient distance so that interaction is impossible and a serious

incident in one area will not involve the other

• installing a screen wall that is a vapour barrier and has an appropriate

- fire resistance level (FRL).

Types of engineering controls include the following:

• totally or partly enclosing the dangerous goods, or external hazard

• adequate ventilation to eliminate flammable or toxic atmospheres (see

further advice in section 9.9)

• blanketing exposed liquid surfaces with an inert atmosphere or sparging

(bubbling gas through the liquid from below)

• automating processes to eliminate human error

• fitting sensors and controls for liquid levels, pressure and temperature

– for example to reduce the risk of overflow, uncontrolled reaction, to

- minimise loss or the formation of hazardous atmospheres

fitting control devices, alarms or shut down devices

• installing appropriately rated (protected) electrical plant and circuitry to

minimise ignition hazards

• providing spill control to contain the largest foreseeable spill and to confine

spills to avoid risks such as contact with incompatible goods or to limit

spread in order to assist fire control (see further advice in section 9.7)

• constructing effective barriers between incompatible goods

• installing detection systems and alarms for hazardous atmospheres and fires

• installing suitable devices to protect installations from external hazards –

such as a crash barrier to protect a storage tank from damage by moving

vehicles

• installing suitable fire control systems, including fire suppression devices

- such as monitors (see chapter 12).

- Reference TQ3.5-- TQ3.5 Storage-handling-dangerous-goods-1354

- TQ3.6 When a number of cables from various circuits are grouped or bundled together what is it necessary to do to the current carrying capacity of circuit conductors

Provide appropriate derating of cables

- TQ3.7 What means are suitable for protecting an installation from the effect of:

- Over-current?

- Fault currents?

Over current relay/ fuse

Over-current protection (fuses or circuit breakers) must be provided. Circuit breakers that combine the functions of an RCD with overcurrent protection respond to both types of fault. ... An RCD helps to protect against electric shock when current flows through a person from a phase (live / line / hot) to earth

Circuit breaker

- TQ3.8 What conditions must be satisfied before being able to remove a barrier that prevents contact with live parts of electrical equipment?

## Deenergized Parts

When employees work on deenergized parts or near enough to them to expose the employees to any electrical hazard they present, the following safety related work practices must be followed:

- Treat as energized any conductors and parts of electrical equipment that have been deenergized, but have not been properly locked out or tagged.

- While any employee is exposed to contact with parts of fixed electric equipment or circuits which have been deenergized, the circuits energizing the parts shall be locked out or tagged or both.  In addition, electrical hazards must be controlled; a qualified person must test the circuit to verify deenergization from all voltage sources.

- Safe procedures for deenergizing circuits and equipment must be determined before circuits or equipment are deenergized.  All electric energy sources must be disconnected.  Control circuit devices, such as push buttons, electric switches, and interlocks must not be used as the sole means of deenergizing circuits or equipment.  Interlocks must not be used as a substitute for lockout and tagging procedures.

- TQ3.9 Simultaneously accessible parts at different voltages must not be within arm’s reach. What does this mean?

TQ3.10 Within what time must an over-current device automatically disconnect a final subcircuit supplying 10A socket outlets?

The maximum disconnection time for a 230 V supply voltage shall not exceed the following:
   (a) 0.4 s for final subcircuits that supply—
        (i) socket-outlets having rated currents not exceeding 63 A; or
        (ii) hand-held Class I equipment; or
        (iii) portable equipment intended for manual movement during use.
   (b) 5 s for other circuits where it can be shown that people are not exposed to touch voltages that exceed safe values.

- TQ3.21List the conditions short circuit protective devices must meet.

## Overload Protection - Coordination of Protective Devices

Overload currents in circuit conductors must be interrupted by a protective device before the overload currents cause a temperature increase that might damage joints, insulation or other material surrounding the conductor.

- TQ3.22 List the ‘recognised’ methods of fault protection.

- Switchgear is a combination of electrical disconnect switches, fuses or circuit breakers used to control, protect and isolate electrical equipment. Switches are safe to open under normal load current, while protective devices are safe to open under fault current

- TQ3.23 Can a device used for protection against automatic disconnection of supply be capable of auto reclosing?

- No unless it includes automatic reclosing unit

- TQ3.24 Under what conditions can a device be of the auto reclose type?

- Temporary fault

- TQ3.25Give an example where an auto reclose device may be required.

- Touching of transmission line conductors under strong wind

- TQ3.26 List four types of devices that could be employed to provide automatic disconnection of supply

- Automatic circuit-breakers with thermomagnetic release

- Automatic circuit-breakers with microprocessor-based electronic relay

- 3.Fuse

- 4.RCD

- TQ3.27 Define an overload current and give an example

- In an electric power system, overcurrent or excess current is a situation where a larger than intended electric current exists through a conductor, leading to excessive generation of heat, and the risk of fire or damage to equipment. Possible causes for overcurrent include short circuits, excessive load, incorrect design, or a ground fault. Fuses, circuit breakers, temperature sensors and current limiters are commonly used protection mechanisms to control the risks of overcurrent.

- TQ3.28 Define short circuit current and give an example.

- A short circuit is simply a low resistance connection between the two conductors supplying electrical power to any circuit. This results in excessive current flow in the power source through the 'short,' and may even cause the power source to be destroyed.

- TQ3.34Fuses and circuit breakers are primarily installed to protect:

[Source: Ref R-3-A Part 1, Section 4- Review Questions Q1 P76]

  - Electrical appliances

  - Electrical cables

  - Electrical loads

  - Persons and livestock

- TA3.35 The element of a high rating HRC fuse is normally comprised of

An HRC fuse is a type of cartridge fuse, in which the fuse element is enclosed within a transparent capsule, usually made up of steatite–a ceramic material having good mechanical strength. Manufacturers are now using epoxy resins instead of ceramic material. The capsule is provided with two end caps. The fuse element is connected between end caps within the body. The whole setup is designed such that it can withstand the high pressure developed under short circuit conditions. Powdered quartz, which acts as an arc extinguishing agent, fills the space between the fuse element and the envelope.

## Fuse Element

Silver or copper is normally used as the fuse element due to its low specific resistance. The fuse element normally has two or more sections joint by means of tin joints. Tin has a lower melting point of 2400 C that is three times lesser than the melting point of silver (980o C). Hence the melting of tin joints prevents the fuse from attaining high temperatures during overload and short circuit conditions.

## Process of Fusing

On the occurrence of a fault, the current flowing through the fuse element exceeds its predefined maximum value and the temperature of the fusing element rises and results in the following:

- Melting of silver elements (pre-arcing)

- Vaporization of the elements (Arcing)

- Fusion of silver vapor and filling powder

- Arc extinction

## Fuse Action

Normally the fuse elements are connected in the middle by a tin bridge. This tin bridge has a precise melting point of 230 oC. Once the temperature of the element rises above this temperature, the tin bridge starts melting. Thereby an arc is established between the molten ends of the fuse element. The temperature produced by the arc is sufficient for the sudden melting of the remaining fuse element. The silver vapor thus produced reacts with the quartz powder filling. The chemical reaction between silver vapor and filling powder establishes a high resistance between ends of the blown out fuse elements.

Gradually, this high resistance changes over into insulator and the current is cut off. A transient voltage is created within the fuse at the instant of fault current interruption. The temperature and the internal pressure of the fuse increase to a higher value.

HRC fuses are sometimes used as backup protection for the circuit breakers. The characteristic of the fuse and the circuit breaker is coordinated as such that all the faults within the range of the circuit breaker are cleared by it, whereas those beyond its range are cleared by the fuse.

Preferred rating of HRC fuses are 2, 4, 6, 10, 16, 25, 30, 50, 63, 80, 100, 125, 160, 200, 250, 320, 400, 500, 630, 800, 1000, and 1250 amperes.

## High rupturing capacity HRC fuses

- TA3.36 The purpose of the silica powder filler in a HRC fuse is:

  - For cooling of the fuse element and to form a high resistance material for current interruption when the element fuses

  - For cooling of the fuse element and to provide mechanical shock absorption for the fuse element

  - To form a high resistance material for current interruption when the element fuses and to provide mechanical shock absorption for the fuse element

  - All three of the reasons covered in choices A, B, and C above

- TQ3.37 If a cable supplying a load that is operating at 50% overload, the power dissipated by the cable will be:

[Source: Ref R-3-A Part 1, Section 4- Review Questions Q3 P76]

  - 25% of its original value

  - 50% of its original value

  - 150% of its original value

  - 225% of its original value

<img src="https://usercontent1.hubstatic.com/9046840_f520.jpg" data-ratio="1.0652985074627" alt=""/>

## High Capacity HRC Cartridge Fuses

This type of fuse was developed by General Electric Company. In this of fuse, the breaking capacity is increased by using two or more separate silver elements in parallel. The sizes of the elements are varied so that the elements fuse in a sequence, one after the other. The body is made up of cylindrical ceramic material and is closed by metallic end caps to which the fuse elements are fixed. The fuse elements are surrounded by silica, which acts as the arc quenching medium. An indicator, normally a fine resistance wire, is connected in parallel to the fuse element. In this type of fuse, the whole fault current is not shed immediately due to the usage of more than one fuse element. This construction avoids voltage transients in the circuit.

## Advantages of HRC fuses

- When compared to other circuit interrupters of same capacity HRC fuses are the cheaper one.

- Simple and easy to install.

- No maintenance required.

- High breaking capacity.

- They are consistent in performance.

- Their inverse time characteristic makes them much suited for overload protection.

- They are capable of clearing high as well as low currents.

- Quick operation.

- They are capable clearing high as well as low currents.

- During severe faults, an HRC fuse breaks the circuit before the peak current of the fault is reached.

## Disadvantages

- These fuses once blown out cannot be reused.

- Causes over heating of adjacent contacts.

- The possibility of interlocking is greater.

- TQ3.38 When installing fuses in a final sub-circuit, the current carrying capacity of the cables are re-rated by a factor of:

[Source: Ref R-3-A Part 1, Section 4- Review Questions Q4 P76]

  - 0.7

  - 0.8

  - 0.9

  - 1.25

- Table 8.2 AS3000

- TQ3.39 From the curves shown of Fig F-3-4-7above and Equation E-3-4-1 determine:

[Source: Ref R-3-A Part 1, Section 4- Exercise 3a and 3b, P73]

  - the current required to operate a 40A fuse in 5 seconds and the required fault loop impedance

  - the current required to operate a 40A fuse in 0.4 seconds and the required fault loop impedance

- TQ3.40From the Table 8.1 of Ref. R-3-C determine the maximum value of fault loop impedance to cause the fuses listed below to operate in the nominated times.

[Source: Ref R-3-A Part 1, Section 4- Exercise 3c, P73]

| Fuse Rating (A) | Required Tripping Time (s) | Max. Fault Loop Impedance () | Current Required to Operate Fuse (A) |
| --- | --- | --- | --- |
| 10 | 0.4 | 6.4 ohm | 230/6.4=35.9A |
| 10 | 5 | 9.2 ohm | 230/9.2=25A |
| 25 | 0.4 | Do yourself | Do yourself |
| 40 | 0.4 | Do yourself | Do yourself |
| 63 | 5 | Do yourself | Do yourself |
| 100 | 5 | Do yourself | Do yourself |

- TQ3.41 final sub circuit supplying 230V, 10A socket outlets is protected by a 20A fuse. If the fault loop impedance of the circuit is 3.1 Ω, will the fuse disconnect the circuit in the required time if there is a fault to earth?.

- It will not operate 0.4 s fuse. It will operate 5s fuse

[Source: Ref R-3-A Part 1, Section 4- Exercise 3d, P74]

- TQ3.42 2.2kW quick recovery water heater is to be installed in the tea room of an existing factory. The nearest distribution board has HRC fuses fitted with spare fuse holders for additional circuits. The TPS cable is to be run through the roof space of the tea room which has thermal insulation installed.

[Source: Ref R-3-A Part 1, Section 4- Exercise “Fuse Selection” , P75]

  - Determine the maximum demand current

  - Select a fuse to protect the circuit

  - Current carrying capacity of cable from Ref R-3-G, assume cable is partially surrounded.

  - Do the values of current comply with IB < IN < IZ ?

  - Does the arrangement comply with I2 <1.45 x IZ ?

  - What is required to ensure the circuit will comply?

  - Assuming 1.5mm2 cable is used, will the arrangement provide short circuit protection?

- TQ43The de-rating factor of 90% for a fuse protected cable is derived from what ratio?

[Source: Ref R-3-A Part 1, Section 4- Review Questions Q7 P77]

IB/IZ

- TQ44What is the maximum acceptable fault loop impedance for a 20A fuse to operate in the specified time of 0.4 seconds?

[Source: Ref R-3-A Part 1, Section 4- Review Questions Q8 P77]

  - ohm

- TQ3.45 Explain what is meant by the term discrimination as applied to circuit protection:

- A circuit breaker is a switching device which can be operated manually and automatically for control and protection of electrical power circuit. ... Discrimination is the coordination between the operating characteristics of circuit breakers placed in series.

- TQ3,46 Explain what is meant by the term trip free as applied to circuit protection?

- A trip-free circuit breaker is a circuit breaker that will trip (open) even if the operating mechanism (ON-OFF switch) is held in the ON position. A nontrip-free circuit breaker can be reset and/or held ON even if an overload or excessive heat condition is present.

- TQ3.47 Explain what is meant by the term prospective fault current:

- Prospective short-circuit current. The prospective short-circuit current (PSCC), available fault current, or short-circuit making current is the highest electric current which can exist in a particular electrical system under short-circuit conditions. It is determined by the voltage and impedance of the supply system

- TQ3.48 Explain what is meant by the term inverse time characteristics

- Inverse time tripping is a characteristic of circuit breakers in which the breaker trips in more time with lower overcurrent, and less time with higher overcurrent. For the US, Article 100 of the National Electric Code defines it as follows: "Inverse Time (as applied to circuit breakers).

- TQ3.49 Explain the action of a magnetic circuit breaker

- Thermal-magnetic circuit breakers contain two different switching mechanisms, a bimetal switch and an electromagnet. ... The bimetal typically sits behind a trip bar and is part of the currentcarrying path. Electrical current exceeding the breaker-overload rating heats the bimetal enough to bend it toward the trip bar

- Using Fig. F-3-5-5 to determine the current causing automatic disconnection of supply for a:

[Source: Ref R-3-A Part 1, Section 5- Review Questions Q12/13/14, P89]

  - 10A type B circuit breaker (0.002s)

  - 10A type C circuit breaker (0.002s)

  - 10A type D circuit breaker (0.01s)

- TQ3.50 A final sub-circuit supplying 230V, 10A socket outlets is protected by a 20A type C circuit breaker. If the fault-loop impedance of the circuit is 2.12 Ω, will the circuit breaker disconnect the circuit in the required time if there is a fault to earth?

Max earth fault loop impedance is 1.5 ohm but it is now 2.1 ohm. CB will not operate

- TQ3.51  A 230V installation is arranged in the following manner:

[Source: Ref R-3-A Part 1, Section 5- Review Questions Q19, P91]

consumer’s mains = 16mm2, length 25 meters

final sub-circuit:

cable = 1.5mm2,2-core + earth, length 15 meters, current rating 13A
load = 2.2kW quick recovery water heater, taking 9.6A
protection = 10A type C circuit breaker
external fault-loop impedance = unknown

Does the circuit arrangement satisfy the requirements of the Rules in terms of:

- coordination between the cable and circuit protective device?

- overload protection?

protection against indirect contact?

IZ = 13A

IN=10A

IB=9.6A  It follows IB<IN<IZ  ( It complies with cable and circuit protective device

Over load I2 = 10A   1.45 IZ = 1.45x 13=18.85A   Thus I2<1,45IZ  ( It complies with Protective device)

- TQ3.52 Using Table 8.1 of AS/NZS 3000:2007 determine the maximum value of fault-loop impedance to cause the circuit breakers listed in the following table to trip in the nominated times. Also determine the current required to operate the circuit breaker.

[Source: Ref R-3-A Part 1, Section 5- Review Questions Q17, P90]

| Circuit Breaker Rating (A) | Circuit Breaker Type | Maximum Fault-Loop Impedance (Ω) | Fault Current Required to Operate Circuit Breaker (A) (show range) |
| --- | --- | --- | --- |
| 20 | C | 1.5 | (230V/1.5 ohm) 20A to 153A |
| 20 | D | Do it yourself | to |
| 25 | B | Do it yourself | to |
| 40 | C | Do it yourself | to |
| 63 | D | Do it yourself | to |
| 100 | C | Do it yourself | to |

- TQ3.53 Use the circuit breaker tripping curves shown below to answer the following:

[Source: Ref R-3-A Part 1, Section 5- Review Questions Q15, P89]

  - Under fault condition a type C, 20A circuit breaker is exposed to 400A.
How long will it take to operate? (Multiple= 400A/2=20) (0.005s)

  - A 10A type C circuit breaker is exposed to 12A.  (Multiple = 12/10=1.2 =3600s)
How long will it take to operate?

  - A 160A type D circuit breaker is exposed to 960A.
How long will it take to operate?

- Multiple=960/160=6

- 1 sec

TQ3.54 In a domestic installation, nominate which circuits require RCD protection

Socket outlets (Clause 2.6)

- TQ3.55 What is the maximum rated residual current of an RCD protecting socket outlets and lighting circuits in a domestic installation?

- Clause 2.6.3.2 requires RCD protection of socket-outlets with ratings up to 20A in installations other than residential. Lighting and directly connected hand held equipment also require RCD protection

2.6.1 General

The use of fixed setting RCDs with a rated operating residual current not

exceeding 30 mA is recognized as providing additional protection in areas

where excessive earth leakage current in the event of failure of other

measures of protection or carelessness by users could present a significant

risk of electric shock.

NOTE: The use of RCDs is intended only to augment other measures of basic

protection.

RCDs do not provide protection against faults between live conductors, nor

do they provide protection against voltages imported into the electrical

installation earthing system through the supply system neutral conductor.

The use of such devices is not recognized as a sole means of protection

and does not obviate the need to apply the protective measures specified in

Clause 2.4.

Additional protection shall be provided, where required by Clause 2.6.3, to

automatically disconnect the supply when an earth leakage current reaches

a predetermined value.

NOTES:

1 The requirements in these rules are for RCDs with a maximum sensitivity of

30 mA (can be either 10 mA or 30 mA).

TQ3.56 Using a voltmeter with an internal resistance of 1000 Ω/volt set to the 250VAC range, calculate the current that would flow if connected between active and earth on a 230V circuit

1000 ohm / volt x 250V = 250000 ohm

I = 230/250000 = 9.2 x 10-4 A  92mA

TQ3.57  Using a voltmeter with an internal resistance of 10 MΩ/volt, calculate the current that would flow if connected between active and earth on a 230V circuit

10M ohm / volt x 230V = 2300 Mohm

I = 230 / 2300 x 106 = 0.1 micro amp

- TQ3.58 From the results of the calculations of Error: Reference source not found and Error: Reference source not found, above, which test instrument would be more suitable for testing the operation of a RCD?

- First one is more suitable 92mA

- TQ3.59 What don’t RCDs provide protection against?

- RCD does not provide protection against unexpected or dangerously high current

- TQ3.60-Where are RCD’s with a sensitivity of 10mA used?

- Type 10mA

Type I RCD is specified for use in patient treatment areas by AS/NZS 3003: Electrical Installations—Patient Treatment Areas of Hospitals and Medical and Dental Practices. This type is also suitable for use in research and educational laboratories. In hospital use, the RCD must trip on a leakage current of no more than 10mA in a time of not more than 40 milliseconds. Because medical equipment might also contain rectifying components, the Type I RCD must also respond to DC pulses. The device must not trip on leakage currents less than 5mA.

Medical treatment quite often requires the patient to be connected to electro-medical equipment, and some procedures might involve the insertion of electrodes into the body. Under these conditions, body resistance is lowered and the probability of fibrillation is greatly increased. The maximum trip time for Type I devices is derived from the duration of the vulnerable period of heart activity.

- TQ3.61 How is the load current rating of an RCD determined?

## RCD and Testing

Before installing an RCD on an existing circuit it is essential to locate and rectify any source of unacceptable leakage current. The procedure when testing for leakage current in a circuit is:

- Supply is turned off

- The main earth and main neutral from the neutral link is disconnected
Appliances can remain connected or disconnected and tested separately.

- An insulation resistance tester set to 500V DC is used to test between the load side of the main switch and the main earth and between the neutral link and main earth.

- If a low reading is obtained, the circuits not intended for RCD protection are isolated and the circuit is tested again. A reading of 1M means there is a leakage current of 0.24mA for a voltage of 240V to earth

- TQ3.62 Do earthing conductors pass through an RCD? Explain

- Earthing conductor does not pass through RCD.

If all the conductors supplying a load are passed through a toroidal core transformer, any earth fault current will be detected by the sensing winding. Therefore the same operating principle applies as described for single-phase AC circuits.

- It is obvious from Figs. F-3-6-3 and F-3-6-4 that, to detect earth fault current, all the live conductors supplying a circuit (actives and neutral) must pass through the device, from supply to load, in the same direction. The term ‘residual’, meaning ‘left over’, refers to the current left over as a result of the phasor sum of the currents in all the conductors passing through the toroidal core.

- TQ3.63 What is a type S RCD used for?

- An S Type RCD is a time delayed RCD that performs very differently to a typical RCD.

Generally, the job of an RCD is to remove power very quickly under fault conditions, hence protecting against electric shock.

An S Type RCD is intended to operate more slowly so as to minimise the risk of nuisance tripping. However, it is important to note that S Type RCDs are not suitable for personal shock protection because they may allow current to flow through the body for an unacceptably long period. Therefore S Type RCDs should not be used to provide personal protection. Their primary function is to provide protection against electrical fire. In many industrial type installations where the main concern is not shock risk but rather fire risk, S Type RCDs are perfectly suited.

Ignition of a fire by an electrical fault current requires a combination of current and time and S Type RCDs are designed with a current/time characteristic built in that ensures that an electrical fire will not occur within the response time of the RCD. The typical response time for a 100ma S Type RCD is in the region of 200 milliseconds for a current of 200 milliamps. It is used for protection against indirect contact with live parts or where a high standing leakage current.

T3.64 For each of the items of equipment listed in the table below, identify if they would be suitable or unsuitable for automatic re-closure of the supply.

[Source: Ref R-3-A Part 1, Section 7-Example 5, P120]

| Equipment | Automatic Re-closure |  |
| --- | --- | --- |
|  | Suitable | Unsuitable |
| Lathe in a fabricating shop |  | X |
| Conveyor in a mail handling center |  | X |
| Air conditioning system | X |  |
| Refrigeration plant for a cool room |  | X |
| Power hacksaw |  | X |
| Sump pump | X |  |
| Fire hydrant booster pump | X |  |
| Lifts in a multi-storey building | X |  |

- TQ3.65 Explain how the DOL starter shown below prevents automatic re-closure of the supply to the motor, following a loss of supply.

[Source: Ref R-3-A Part 1, Section 7-Example 6, P121]

- Class Lesson

- TQ3.66 What conditions could warrant the installation of SPD’s

Fig. F-3-7-2(a) Switchboard Type Surge Protector

If adequate protection is not installed, voltage surges may damage sensitive electronic equipment such as computers, televisions and videos. Appendix F of Ref R-3-C supplies guidelines for the installation of Surge Protective Devices (SPD’s)

TQ3.67 What is the best primary location for the installation of SPD’s

Primary protection is applied to incoming services such as power on the main switchboard and the telephone MDF

TQ3.68

The Surge Protection Device (SPD) is a component of the electrical installation protection system. This device is connected in parallel on the power supply circuit of the loads that it has to protect (see Fig. J17). It can also be used at all levels of the power supply network.