- A light source produces a luminous flux of 1000 lumens. If all of the produced light falls onto a surface having a surface area of 10 square metres, determine the illuminance on the surface.

I                      100

E = ------------- = ------------------- = 10 lux

A                      10

- A room with a floor measuring 3 metres by 5 metres is to be lit lo an illuminance of 200 lux. Assuming all the light produced by the source reaches the floor, calculate the necessary luminous flux to achieve this.

I                      I

E = ------------- = ------------------- =200                 I = 200 x 15 = 3000 cd

A                      3 x 5

- A 40 watt fluorescent lamp produces 1000 lumens when supplied with the correct voltage. What is its luminous efficacy?

Where:

h = Luminous Efficacy in lm/W

F = Luminous Flux in lm

P = Input power in watts (W)

E.7.1.3

1000

n=----------------------- = 25

40

- Calculate the illumination on a surface that is 3m distant from a 200cd light source.

- I                   200

- E=------------------ =----------------=22.2 lux

- d  2                            32

- TQ 7.5 / 7.6 Do it yourself

- TQ7.7     A 2500cd light source is mounted 4m above the floor. Calculate the illumination:

[Source: Ref R.7.A Part 2, Section 8- Example 9, P143]

  - on the floor directly below the light

  - a point on the floor 3m distant from directly beneath the light

200                              200

E=--------------------------------=---------------------= 12.5 lux

42                                                         16

tan Ǿ= 3/4 -0.75 =  ---------------------   Ǿ= 36.8

E=   12.5 Cos Ǿ = 12.5 x 0.8 = 10 lux

- TQ 7.8 What is the difference between the working plane and the task area?
Give an example.

The working plane in office area is considered 0.75 or 0.8 form floor level which is the

standard height of a table.

When standard is asking for 500 Lux it should be achieved at this height for the office area.

In this guide 0.75 will be considered as the height for the office area.

The working plane for a corridor is 0.2

Task area is the most important space in terms of illumination quality. Here the work itself takes place and at the very least demands constant and sufficient lighting without any disturbing effects such as glare or flicker. The illumination of the task area should take into account the type of work being done, the focus it takes to carry out the task and also other demands. For example graphic-intensive work or any other visually engaging activity requires high-quality colour rendering.

For the designer this means having higher-quality light sources in mind, for the manager it means higher costs and extra care in maintenance. Replacing of the light source with an inferior type during maintenance could negatively affect the quality of the product or service, jeopardizing sales and increasing unnecessary costs.

The standard requires constant illumination level over a task area regardless of quality or age of the lighting system. Special care therefore has to be taken that even older light sources, which diminish their illuminance with age, provide the required illumination level. If necessary, for certain tasks additional luminaires may be needed in the task area.

TQ7.9 Name the three basic types of reflectors

Specular

Diffuse

Spread

- TQ7.10 With regard to lighting, what are the basic factors that have an effect on the visual comfort of people?

### Factors Affecting the Visual Task

There are a number of factors that have an effect on the visual comfort of a person performing/working to complete a task. These are:

- Task illuminance

- Task contrast

- Glare

### Task Illuminance

There must be sufficient light so that the required work can be carried out correctly and efficiently.

Low lighting levels causes eye strain and fatigue and may even compromise workplace safety

Too high a lighting level causes eye strain (sometimes pain), unsafe working conditions and inefficient completion of tasks. Examples of high lighting levels are working on or near the light sources, direct summer sunshine or working near arc welders.

AS 1680 details the correct Illuminance values for the task, e.g. classroom 400 lux, fine detail (watch making) up to 3000 lux.

### Task Contrast

Contrast is the difference in luminance and/or colour that makes an object (or its representation in an image or display) distinguishable

### Glare

Glare is caused by the brightness of a background or object in the person’s field of vision, which distracts that person voluntarily and involuntarily from the visual task.

Glare is categorised as:

- Discomfort glare - actual discomfort of the person but may not impair the visibility of the task.

- Disability glare - may not cause discomfort to the person but impairs the visibility of the task.

- Direct glare - the light source is in the field of vision of the person

- Indirect glare - this is the reflection of a light source from a surface or object in the field of vision of the person

Glare is very subjective and is dependent upon the ambient light (night or day etc.), the surface finish of the objects in the field of view, the physical condition of the observer (age, health, fitness, fatigue etc.) and location of light sources.

### Tutorial 7.2

- TQ11 What principle is used in GLS lamps to create artificial light?

The incandescent GLS (General Lamp Shape) light bulb was the mainstay of domestic lighting for many years. Since the ban on these energy wasting lamps came into force it has been difficult to find an energy saving alternative for the traditional Classic Shape
An incandescent light bulb, incandescent lamp or incandescent light globe is an electric light with a wire filament heated to such a high temperature that it glows with visible light (incandescence). The filament is protected from oxidation with a glass or fused quartz bulb that is filled with inert gas or a vacuum. In a halogen lamp, filament evaporation is slowed by a chemical process that redeposits metal vapor onto the filament, thereby extending its life.

The light bulb is supplied with electric current by feed-through terminals or wires embedded in the glass. Most bulbs are used in a socket which provides mechanical support and electrical connections.

Incandescent bulbs are manufactured in a wide range of sizes, light output, and voltage ratings, from 1.5 volts to about 300 volts. They require no external regulating equipment, have low manufacturing costs, and work equally well on either alternating current or direct current. As a result, the incandescent bulb is widely used in household and commercial lighting, for portable lighting such as table lamps, car headlamps, and flashlights, and for decorative and advertising lighting.

Incandescent bulbs are much less efficient than other types of electric lighting; incandescent bulbs convert less than 5% of the energy they use into visible light,[1] with standard light bulbs averaging about 2.2%.[2] The remaining energy is converted into heat. The luminous efficacy of a typical incandescent bulb is 16 lumens per watt, compared with 60 lm/W for a compact fluorescent bulb or 150 lm/W for some white LED lamps.[3]

Some applications of the incandescent bulb (such as heat lamps) deliberately use the heat generated by the filament. Such applications include incubators, brooding boxes for poultry,[4] heat lights for reptile tanks,[5] infrared heating for industrial heating and drying processes, lava lamps, and the Easy-Bake Oven toy. Incandescent bulbs typically have short lifetimes compared with other types of lighting; around 1,000 hours for home light bulbs versus typically 10,000 hours for compact fluorescents and 30,000 hours for lighting LEDs.

- TQ7.12What principle is used in Fluorescent lamps to create artificial light?

- fluorescent lamp, or fluorescent tube, is a low-pressure mercury-vapor gas-discharge lamp that uses fluorescence to produce visible light. An electric current in the gas excites mercury vapor, which produces short-wave ultraviolet light that then causes a phosphor coating on the inside of the lamp to glow. A fluorescent lamp converts electrical energy into useful light much more efficiently than incandescent lamps. The typical luminous efficacy of fluorescent lighting systems is 50–100 lumens per watt, several times the efficacy of incandescent bulbs with comparable light output. What is the material used for the filament of an incandescent lamp?

[Based on: Ref R.7.A Part 2, Section 9- Review Questions, Q3, P175]

- TQ7.13 What is the material used for the filament of an incandescent lamp?

Tungsten

- TQ7.14 When supplied with nominal voltage, what is the approximate filament temperature of a quartz halogen lamp?

- This is the temperature in K (Kelvin) of a full radiator (black body), which emits light of similar color balance (chromaticity) as the tungsten halogen lamp. It is a recognized mathematical best match. For a filament temperature of 3300 K, the color temperature is approximately 3390 K.

- A halogen lamp, also known as a tungsten halogen, quartz-halogen or quartz iodine lamp, is an incandescent lamp consisting of a tungsten filament sealed into a compact transparent envelope that is filled with a mixture of an inert gas and a small amount of a halogen such as iodine or bromine. The combination of the halogen gas and the tungsten filament produces a halogen cycle chemical reaction which redeposits evaporated tungsten to the filament, increasing its life and maintaining the clarity of the envelope. Because of this, a halogen lamp can be operated at a higher temperature than a standard gas-filled lamp of similar power and operating life, producing light of a higher luminous efficacy and color temperature. The small size of halogen lamps permits their use in compact optical systems for projectors and illumination. What is the approximate useful life of a fluorescent lamp, supplied with the correct voltage as nominated by manufacturers?

[Based on: Ref R.7.A Part 2, Section 9- Review Questions, Q9, P176]

- TQ7.15 What is the approximate useful life of a fluorescent lamp, supplied with the correct voltage as nominated by manufacturers?

- Incandescents typically lose 10% – 15% of their initial lumen output over an average lifetime of 1,000 hours. ... High-quality fluorescent lamps using rare earth phosphors lose only 5% – 10% of initial lumens over 20,000 hours of operation

- TQ7.16 What are two advantages of using an inert gas inside the bulb of an incandescent lamp?

###### Advantages are:

- Inert gas in cargo tank make atmosphere non-explosive.

- It allows high-pressure tank washing and reduces tank-cleaning time.

- It allows COW( crude oil washing)

- Reduces corrosion in tanks – with an efficient scrubber in the system.

- Improves stripping efficiency and reduces discharge time.

- Aids the safe gas freeing of tanks.

- It is economical to operate.

- It forms a readily available extinguishing agent for other spaces.

- Reduces the loss of cargo through evaporation.

- Complies with legislation and reduces insurance premiums

- TQ7.17 What are two advantages of Q-I lamps compared to GLS lamps?

- The Linear Halogen QI 255mm 1000w Lamp is commonly used in flood lights, food warming bainmaries and many general lighting applications.  This Quartz Iodine (QI) Lamp is equipt with UV stop, which protects against harmful radiation.

- TQ7.18 Briefly explain in your own words the halogen regenerative cycle.

- Halogen Regenerative Cycle. ... Thermal gradients formed as a result of the temperature differential between the hot filament and the cooler envelope contribute to interception and recycling of tungsten to the lamp filament through a phenomenon known as the halogen regenerative cycle.

- wireless power transfer using inductive charging over distances of up to 4 cm (1.6 inches

[Based on: Ref R.7.A Part 2, Section 9- Review Questions, Q1, P177]

- TQ7.19 What is the colour of a LED determined by?

- The popular colors available for LEDs are "warm white" or "soft white," and "bright white." Warm white and soft white will produce a yellow hue, close to incandescents, while bulbs labeled as bright white will produce a whiter light, closer to daylight and similar to what you see in retail stores Give two methods of creating white light with LEDs and give an advantage and disadvantage of each method?

- The two main types of LEDs presently used for lighting systems are aluminum gallium indium phosphide (AlGaInP, sometimes rearranged as AlInGaP) alloys for red, orange and yellow LEDs; and indium gallium nitride (InGaN) alloys for green, blue and white LEDs. What voltage and current does an illumination grade LED require to operate correctly?

[Based on: Ref R.7.A Part 2, Section 9- Review Questions, Q12, P208]

- TQ7.20 Give two methods of creating white light with LEDs and give an advantage and disadvantage of each method?

- Phosphor-converted white light: Another approach to generating white light is by use of phosphors together with a short-wavelength LED. For example, when one phosphor material used in LEDs is illuminated by blue light, it emits yellow light having a fairly broad spectral power distribution. Blue pollution: Because cool-white LEDs (i.e., LEDs with high color temperature) emit proportionally more blue light than conventional outdoor light sources such as high-pressure sodium lamps, the strong wavelength dependence of Rayleigh scattering means that cool-white LEDs can cause more light pollution than other ...

1.2 Advantages of using LEDs

> LEDs produce more light per watt than do incandescent bulbs; this is useful in battery powered or energysaving devices.

> LEDs can emit light of an intended color without the use of color filters that traditional lighting methods require. This is more efficient and can lower initial costs.

> The solid package of the LED can be designed to focus its light. Incandescent and fluorescent sources often require an external reflector to collect light and direct it in a usable manner.

> When used in applications where dimming is required, LEDs do not change their color tint as the current passing through them is lowered, unlike incandescent lamps, which turn yellow.

> LEDs are ideal for use in applications that are subject to frequent on-off cycling, unlike fluorescent lamps that burn out more quickly when cycled frequently, or HID lamps that require a long time before restarting.

> LEDs, being solid state components, are difficult to damage with external shock. Fluorescent and incandescent bulbs are easily broken if subjected to external shock.

> LEDs can have a relatively long useful life. Reports estimates 60,000 hours of useful life, though time to complete failure longer.2 Fluorescent tubes typically are rated at about 30,000 hours, HID and MH are rated anywhere between 10,000 and 24,000 hours and incandescent light bulbs at 1,000–2,000 hours.

> LEDs mostly fail by dimming over time, rather than the abrupt burn-out of incandescent or HID bulbs.3 This provides extra safety for any area illuminated by LEDs. Even if the LEDs dim over time, they never fail completely like HID sources before needing to be replaced. LEDs need to be replaced only after they reach 30% lumen depreciation (17-20 years for quality LEDs).

> LEDs light up very quickly. A typical red indicator LED will achieve full brightness in microseconds; Philips Lumileds technical datasheet DS23 for the Luxeon Star states "less than 100ns." LEDs used in communications devices can have even faster response times.

> LEDs can be very small and are easily populated onto printed circuit boards.

> LEDs do not contain mercury, unlike compact fluorescent lamps.

1.3 Disadvantages of using LEDs

> On an initial capital cost basis, LEDs are currently more expensive, measured in price per lumen, than more conventional lighting technologies. The additional expense partially stems from the relatively low lumen output, combined with the cost of the drive circuitry and power supplies needed. However, when considering the total cost of ownership (including energy and maintenance costs), LEDs far surpass other sources. In December 2007, scientists at Glasgow University claimed to have found a way to make Light Emitting Diodes brighter and use less power than energy efficient light bulbs currently on the market by imprinting holes into billions of LEDs in a new and cost effective method using a process known as nanoimprint lithography.4 Around the same time, in Montreal Canada, Lumec inc. developed an LED light engine that consumes 20% to 30% less energy than HPS (high pressure sodium) and 40% to 50% less than MH (metal halide) while delivering comparable photometric performance, if not better, than HID lights.

> LED performance largely depends on the ambient temperature of the operating environment. Driving the LED hard in high ambient temperatures may result in overheating of the LED package, eventually leading to device failure. Adequate heat-sinking is required to maintain long life. This is especially important when considering automotive, outdoor, medical, and military applications where the device must operate over a large range of temperatures, and is required to have a low failure rate. The most heat resistant LEDs available commercially, such as those used by Lumec inc. In their light engine, the LifeLEDTM can function at optimal efficiency from -40°C to +50°C(-40°F to 122°F).

- TQ7.21 What voltage and current does an illumination grade LED require to operate correctly?

Many circuits operate LEDs at less than the recommended maximum current, to save power, to permit the use of a standard resistor value, or to reduce brightness. Typically, the forward voltage of an LED is between 1.8 and 3.3 volts

single green LED with 10mA forward current should have a constant operating voltage of 5V, the series resistor RV equals (5V -VF,10mA)/10m

- TQ7.22 Briefly explain how pulse width modulation can be used to dim LEDs

- Pulse Width Modulation or PWM is a term you hear a lot if you are interested in controlling power output using a microcontroller. It has many applications, although one of the most popular amongst hobbyists is controlling the brightness of LEDs.Apr What are the requirements of AS3000 with regards to the location of low voltage lamp holders in order protect against inadvertent contact with live parts? (Quote Clause Number)

If we were to dim an LED by reducing the source voltage for the LED, this could create a change in color and would not be a consistent degree of fading across all LEDs.  The proper way to dim an LED is by turning it on or off very quickly so that the human eye cannot see the blink rate.  The frequency of the PWM waveform is not important as long as it is faster than the human eye can see and not too fast that the LED fails to reach its saturation voltage.  The duty cycle of the PWM waveform is used to set the brightness of the LED.

Various Duty Cycle Waveforms

We could create all of these PWM waveforms through ordinary GPIO sets in firmware as we have used previously to turn on or off the LEDs, but setting GPIOs in firmware takes a lot of time and is vulnerable to the same software-timing issues mentioned previously in this lesson.  For example, take this small snippet of code, which is the quickest possible way to control GPIOs in firmware.  I am using the memory mapped method to set and clear the GPIO, which avoids function calling overhead.

GPIO_PinModeSet(LED_PORT, LED_PIN, gpioModePushPull, 0);

uint64_t timer = get_time_in_ms();

for (int i= 0; i < 10000; i++)

{

GPIO->P[LED_PORT].DOUTSET = 1 << LED_PIN;

GPIO->P[LED_PORT].DOUTCLR = 1 << LED_PIN;

}

timer = elapsed_ms(timer);

The value found in the timer variable after the for loop completes is 19ms to run this simple GPIO set and clear loop 10,000 times.  That is equivalent to 10,000 cycles / .019s = 526315Hz or ~ 0.5MHz.  That is orders of magnitude greater frequency than we need for LED dimming, but much slower than the hardware is capable of driving.  Remember, the hardware can run at many times that frequency, so controlling things at the hardware level strictly from firmware will always run slower than dedicated hardware peripherals.

Rather than control the LED dimming strictly from firmware, I will configure hardware timers to control the GPIOs directly.  We must first write firmware to initialize the timer and the PWM GPIO functions, and then the hardware automatically repeats the sequence forever, freeing your firmware to do other things.  We don’t need that faster hardware rate for our LED dimming project, but there are other applications that would benefit from the faster switching rate.

Let’s configure the peripheral timer to PWM a GPIO and set up a programmable duty cycle to be output to the TEST_LED0 on the Starter Kit.  If you recall, TEST_LED0 is on port E, pin 2.  I need to make sure that there is a timer that can be configured to output to PE2.  By looking at the Data Sheet for the Wonder Gecko that is on our kit, I find this GPIO is routed from TIMER3, Channel 2, on Location 1:

- TQ7.23 What are the requirements of AS3000 with regards to the location of low voltage lamp holders in order protect against inadvertent contact with live parts? (Quote Clause Number)

4.5 LIGHTING EQUIPMENT AND ACCESSORIES

* 4.5.1 Lampholders, including lampholders incorporated in a luminaire

4.5.1.1 Location

All lampholders shall be located to be adequately protected against

damage that might reasonably be expected.

In order to protect against inadvertent contact with live parts, low voltage

lampholders shall be located to minimize the risk of—

(a) direct contact with live parts of a lampholder when the lamp is

removed; and

(b) mechanical damage to the lamp or lampholder.

These requirements may be satisfied by—

(i) installation not less than 1.8 m above the ground, floor or platform; or

(ii) provision of a suitable guard for the lamp and its lampholder.

A pendant lampholder shall not be exposed to the effects of significant

movement of air, e.g. outdoors or where exposed to the operation of fans,

etc.

- TQ7.24 What are the requirements of AS3000 with regards to locating lamps near flammable materials? (Quote Clause Number)

| - 4.5.2.3 Recessed luminaires - 4.5.2.3.1 General requirements - (a) Recessed luminaires and their auxiliary equipment shall be installed in - a manner designed to prevent— - (i) excessive temperature rise of the luminaire and auxiliary equipment; and - (ii) the risk of fire from ignition of combustible materials. - (b) The requirement in (a) shall be satisfied by one of the following methods: - (i) The installation of a luminaire designed and certified by the manufacturer as being suitable for operation— - (A) in contact with combustible materials; or - (B) in contact with, or enclosed/covered by, thermal insulation material. - (ii) The installation of a luminaire in combination with a barrier tested and classified in accordance with AS/NZS 5110 as being suitable for the installation conditions. - (iii) The installation of a luminaire with separation from thermal insulating materials, combustible building elements and loose combustible materials not less than— - (A) the minimum clearance specified by the manufacturer of the luminaire, which may require a barrier or guard constructed of fire-resistant materials; or - (B) the default clearances as specified in Figure 4.9, which may require a barrier or guard constructed of fire-resistant materials. |  |
| --- | --- |

- TQ7.25 Why do HID lamps, under standard conditions, take time to re-strike after being turned off?

##### What are warm-up and restrike times for metal halide lamps?

Metal halide (MH) lamps do not achieve their full light output immediately after starting. Rather, they require a period of time-1 to 15 minutes-to reach 90% of their full light output. This period is called the warm-up (or run-up) time. After a lamp has been on for a period of time and then extinguished, it cannot be immediately turned back on. Before the lamp can be turned back on, the arc tube must have a chance to cool down or the lamp will not restart. This period of time is called the restrike time. Restrike times for traditional probe-start MH lamps can take 15 minutes or longer, but restrike times for pulse-start MH lamps are generally much shorter (see Figure 4). According to manufacturers' literature, restrike times for pulse-start MH lamps can be more than twice as fast as for probe-start MH lamps.

Figure 4. Warm-up/restrike times for probe-start and pulse-start technologies

- TQ7.26 What is the efficacy the following light sources?

[Based on: Ref R.7.A Part 2, Section 9- Review Questions, Q10, P216]

  - High Pressure Mercury Vapour

  - Metal Halide

  - High Pressure Sodium

  - Low Pressure Sodium

The lumen ratings of Mercury Vapor lamps are based on the average performance of large groups of lamps operating at rated watts in the specified operating position on a standard reference reactor or ballast. In this table, the range of Mercury Vapor lamp efficacies is compared to the efficacies of other light sources.

| Lamp Type | Wattage Range | Initial Efficiency (Lumens per Watt) |
| --- | --- | --- |
| Mercury Vapor | 40-1000 | 32-63 |
| MV Self-ballasted | 160-750 | 14-24 |
| Fluorescent | 15-215 | 55-100 |
| Incandescent | 6-1500 | 4-20 |
| Tungsten Halogen | 50-1500 | 18-22 |
| High Pressure Sodium | 35-1000 | 40-140 |
| Metal Halide | 70-1500 | 80-125 |
| Low Pressure Sodium | 18-180 | up to 200 |

## Tutorial 7.3

- TQ7.27Typically, fluorescent lighting is not used for illumination with mounting heights greater than:

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q5, P247]

  - 2.4 m

  - 3 m

  - 6 m

  - 10 m

Luminaires housing one or more tubular fluorescent lamps are most frequently used in commercial lighting installations (shops, offices, educational institutions, etc.) and industrial where the mounting height is less than about 6 metresMounting height is critical: for sconces with an indirect lighting component, mounting height should always be high enough that the lamp is concealed from view to prevent direct glare. Install the outlet box for the luminaire at least 5.5 feet above the floor.

- Wall-Mounted

www.lrc.rpi.edu/resources/publications/lpbh/075WallMounted.pdf

Feedback

About this result

## People also ask

What height to mount wall lights?

Generally wall sconces are installed at a height of 66 inches to 72 inches (5.5 feet to 6 feet) above floor level (rooms with vaulted ceilings can take a higher placement). However, if the average height of people living in your home is well above 6 feet – or below five and a half, you may want to adjust accordingly!

- Best Height and Placement for Your Wall Sconce - Pegasus Lighting

https://www.pegasuslighting.com/learn.../best-height-and-placement-for-your-wall-sconc...

Search for: What height to mount wall lights?

How high should an outdoor light be mounted?

In addition to size, the height of the fixture is another important consideration. As a general rule of thumb, outdoor entryway lights should be positioned at eye level. More specifically, the center of the light source should measure 5.5 to 6.0 feet from the ground. Fixtures also should be mounted 8-10 feet apart.Sep 16, 2015

- Size Matters: How to determine fixture-to-house proportion for outdoor ...

https://progresslighting.com/size-matters-how-to-determine-fixture-to-house-proportion-...

Search for: How high should an outdoor light be mounted?

How high do you hang a wall sconce?

Suggested placement heights range from 60-to-72 inches above the floor. For a room with 8-foot ceilings, place sconces between 60 and 66 inches high; place them 66-to-72 inches high in rooms with ceilings over 9 feet.

- Where to Hang Dining Room Wall Sconces | Home Guides | SF Gate

homeguides.sfgate.com/hang-dining-room-wall-sconces-61971.html

Search for: How high do you hang a wall sconce?

How high should a wall light be?

As a very general rule position your wall lights about 152cms or 60" above floor level. If you are putting wall lights in a long hallway or corridor a general rule of thumb is to position them about 250 to 300cms or between 8' to 10' apart.

- What is the best height for wall lights? - The Lighting Company

https://www.lightingcompany.co.uk/what-is-the-best-height-for-wall-lights-i88

Search for: How high should a wall light be?

How high is a vanity light?

It should be placed 75 to 80 inches above the floor and, like all vanity lighting, contain at least 150 watts — ideally spread over a fixture that's at least 24 inches long so that the light will wash evenly over the hair and face. The shower is a secondary area of task lighting

- TQ7.28 A lighting system whereby 80% of the light reaches the surface classified as directly from the source is termed:

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q6, P248]

  - Direct lighting

  - Semi-direct lighting

  - Direct-indirect lighting

  - Semi-indirect lighting

#### Direct:

Highest luminaire efficiency; maximum light directed toward the working plane with minimum loss to other surfaces; high level of contrast (shadows).

- 0 - 10% of received light is reflected from surfaces

- 90 - 100% of the light received is direct from the source

#### Semi-direct:

Lower luminaire efficiency; upward light reflected from ceilings and walls provides softening of shadows

- 10 - 40% of received light is reflected from surfaces

- 60 - 90% of the light received is direct from the source

- TQ7.29The least efficient light fitting is one that uses a/an:

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q7, P248]

  - opalescent diffuser

  - square mesh louver

  - prismatic diffuser

  - painted reflector

- prismatic diffuser (refractor): These are usually of clear or opalescent plastic material constructed to give the light some directional characteristics, whilst reducing the luminance of the lamps in any direction which would produce glare discomfort. (See Figure F.7.3.2 (b))

- opalescent diffusers: Light output from a luminaire through these panels will be virtually uniform in all directions. The luminaire efficiency will be lower (low directional control), and a wraparound type diffuser will produce a luminaire with the lowest shadow effect. (See Figure F.7.3.2 (c))

- TQ7.30A high bay fitting that has an approximate beam spread of 40 to 60 is called a:

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q8, P248]

  - concentrating fitting

  - medium spread fitting

  - spread fitting

  - wide spread fitting

| HID Luminaire Class | Approx. Beam angle | Space-Height Ratio |
| --- | --- | --- |
| Highly Concentrating | up to 30 | Up to 0.5 |
| Concentrating | 30 to 40 | 0.5 to 0.7 |
| Medium Spread | 40 to 60 | 0.7 to 1.0 |
| Spread | 60 to 100 | 1.0 to 1.5 |
| Wide Spread | Greater than (>) 100 | Greater than (>) 1.5 |

- TQ7.31 The recommended cut off angle for luminaires used in classrooms is approximately:

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q10, P248]

  - 50 to 60

  - 60 to 70

  - 40 to 50

  - 70 to 80

Figure F.7.3.5 - Reproduction of Table 8.1 from AS/NZS 1680.1:2006

Showing Recommended Cut-Off Angles For Partially Enclosed Luminaires

- TQ7.32 Name two situations that require specially constructed luminaries

Some situations require specially constructed luminaires:

- hazardous areas luminaires for areas where explosive gases, vapours or volatile liquids are present may be either pressure-resisting encapsulation or increased safety type. (For specific information refer to Ref R.7.C and AS 2381.1)

- Damp situations and dust laden atmospheres laundries, shower rooms, wood machining plants and flour mills are areas which require gasketed luminaires. (For specific information refer to Ref R.7.C)

- TQ7.33 What is a lamellae louver?

- lamellae - strips positioned at right angle to the axis of the lamp and produce longitudinal screening only; often used on luminaires which employ mirror reflectors; lateral screening is provided by the lower edge of the reflectors or wall of luminaire. (See Figure F.7.3.2 (a))

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q14, P249]

Figure F.7.3.2 (a) lamellae diffuser

- TQ7.34Identify four advantages of using electronic ballasts in fluorescent luminaires instead of electromagnetic types.

Some of the other benefits of electronic ballasts, compared to magnetic ballasts, include:

- Reduced heat.

- The need for fewer ballasts.

- Instant start, and programmed start options.

- They're easy to dim.

- There's no humming or flickering.

- They produce steady light and fade less over time

- TQ7.35

- What is the difference between the shielding angle and the cut-off angle of a luminaire?

[Based on: Ref R.7.A Part 2, Section 11- Review Questions, Q15, P249]

# Shielding angle

The glare rating of a lighting installation according to the UGR method is based on the average luminance of the luminaires in the direction of the observer’s eye and not on the lamp or illuminant luminance, which is a lot higher most of the time. For luminaires where illuminants or parts thereof are directly visible from the critical viewing angle range for direct glare, glare and thus a decrease in visual performance can occur in spite of positive glare limitation ratings. In order to limit this glare caused by increased individual illuminant luminance as well, the illuminants must be shielded through suitable measures. The degree of shielding is characterised by the shielding angle, which must comply with various minimum values (table 1.8) according to the illuminant’s luminance

luminance.

Table 1.8: Minimum shielding angle according to EN 12464-1 for definite illuminant luminance values

According to EN 12464-1 the shielding angle is the angle between horizontal plane and viewing direction underneath which the luminous parts of the lamps/illuminants in the luminaire are just visible. According to this definition, only viewed, luminous lamp parts are rated, not bright luminaire surfaces (fig. 1.22). This angle is also called upper shielding angle according to EN 12665 (see also chapter 1.2.1).

It must be distinguished from the cut-off angle of a luminaire between the downward vertical and the direction from which the illuminants and the surfaces of high luminance are just not visible, which is defined in EN 12665. When determining the cut-off angle according to EN 12665, surfaces of high luminance need to be considered in addition to the luminance of the illuminants. The lower cut-off angle α depicted in fig. 1.23 according to EN 12665 only applies, e.g. to narrow-distribution specular reflectors which mostly feature a rather low luminance in the viewing direction. A white reflector would have high luminance which means the shielding angle would be roughly 90°.

For the illuminant luminance values specified in table 1.8, the corresponding minimum shielding angle according to the definition in EN 12464-1 must be observed for the luminous parts of the illuminants only. The values do not apply for luminaires with exclusive light emission into the upper half-space or for luminaires mounted below eye-level.

Luminance values for commercially available lamps are listed in table 1.9. The luminance of a single white LED depends on the angle (see also chapter , "LED lamps"), however, it would usually exceed the limit value of 50 kcd/m2 under flat angles of  ≤ 15° as well as the limit value of 500 kcd/m2 for angles of  ≤ 30°. This leads to non-permissible glare. When looking directly (under 90°) into the LED, values > 10.000 kcd/m2 are reached.

For LED luminaires, the height of the directly visible individual luminance values depends on the structure of the inserted LED modules or the luminaire. The luminaire manufacturer must ensure that the visible luminous surfaces comply with the requirements of EN 12464-1 (see table 1.8). To achieve this, it is possible to insert e.g. a diffuser or a lens to flare LED luminance (see also figure 1.24). Open individual LEDs are only used in luminaires for high mounting heights

Figure 1.22: Definition of the shielding angle for luminous lamp parts according to EN 12464-1 in reference to the horizontal.

Figure 1.23: Definition of the cut-off angle for luminous lamp parts and luminous parts of e.g. reflectors according to EN 12665 in reference to the vertical

- TQ7.36 What voltage is required to ignite a high pressure sodium lamp from a cold start and how is this voltage provided?

- Standard lamps with standard igniters re-ignite after 60 to 90 seconds requiring 2kV to 5kV to ignite from a cold start depending on the lamp specifications. High pressure sodium lamps can only be re-ignited hot if they are of linear double ended construction because hot re-strike requires 18kV to 25kV peak starting pulses.

#### Example:

A general open plan office has dimensions 12 x 8.5 x 2.8 m. The required illuminance is 320 lux. The reflectance of the ceiling is known to be 0.70 and the reflectance of the wall is 0.50 m. The work areas (desks) are at a height of 0.80 m. The luminaires chosen are twin tube, with each tube being 36W ‘daylight’ 2850 lumens, direct-indirect type with UF data as shown in Table 7.4.1 above.

Determine the Number of luminaires required.

##### Solution:

Illuminance:	E = 320 lux

Area:	A = (12  8.5) m2

Lamps per luminaire:	n = 2

Lamp lumen output:	F = 2850 lumens

Maintenance Factor:	MF = 0.8 (as no other data available)

The mounting height is: 	hm = 2.8 - 0.8 = 2.0 m.

The Room Index is:

From Table 7.4.1 with K = 2.5, C = 0.7 & W = 0.5 the UF is found to be 0.55.

Then:

In this case the number of luminaires actually installed might be 15 in 3 rows of 5.

## The Lumen Method

The basis of the lumen method is the following equation:

Where:

| N | = | Number of luminaires required; |
| --- | --- | --- |
| E | = | required illuminance (lux); |
| A | = | Area to be lit; |
| n | = | number of lamps per luminaire; |
| F | = | lamp lumen output (lumens); |
| MF | = | Maintenance Factor This is a combination of three factors: - Dust and dirt inside luminaire surfaces, - Aging of light bulbs, - Cleaning of room surfaces; |
| UF | = | Utilisation Factor This is a function of the luminaire properties and room geometry |

## Required Illuminance (E)

This is the illumination required at the work surface. The Australian Standards 1680.2 series give recommendations for illuminance levels for various types of areas. Separate publications in the series cover General Areas, Office, Industrial, Hospital and Schools. As well as stating recommended illuminance levels, the tables in these publications give recommended colour rendering and maximum glare index. For example recommended illumination for a general office area is given as 320 lux, while the general work area in a Bakery requires 160 lux.

### Area to be Illuminated (A)

This is the task area – not necessarily the floor area.

### Number of Lamps per Luminaire (n)

Many luminaires have more than just the one lamp especially fluorescent luminaires which may have one, two, three, four or more lamps.

### Lamp Lumen Output (F)

This information is supplied by the lamp manufacturer in catalogues or separate data sheets. The table below is a typical fluorescent lamp data table from “Osram Lighting”.

### Maintenance Factor (MF)

The Maintenance Factor, or Light Loss Factor (LLF) is a value between 0 and 1, designed to account for the reduction in light output from a lighting system due to: the ageing of the lamps and the accumulation of dirt and dust on the light fittings and room surfaces. The MF can be affected by:

- degradation of lamp output over time.

- Lamp survival factor – this accounts for the failure of lamps over time, if failed lamps are replaced immediately this factor can be ignored.

- Luminaire maintenance factor – accounts for dirt and dust accumulation on the luminaire.

In the absence of any data or maintenance plans a value 0.8 can be used as ‘safe’ value of MF.

### Space to Height Ratio (SHR)

This is simply the Nominal Spacing to Height ratio. For example an SHR of 1.75 to 1 means that for every 1 metre of mounting height above the work plane there should be a maximum 1.75 metres between fittings.

### Utilisation Factor (UF)

This is a value between 0 and 1, or sometimes given as a percentage, that represents the percentage of total lamp lumens in the room that fall on the work plane. It takes into account the room reflectances, room shape, polar distribution and light output ratio of the fitting.

The steps in determining UF are:

- Determine the Room Index:
This is a number that describes the ratios of the rooms length, width and height and can be calculated from the following formula:

where:

| K | = | Room Index (calculation will usually result in a number between 0.75 and 5) Note that any number outside this range will make this method invalid |
| --- | --- | --- |
| L | = | Length of room |
| W | = | Width of room |
| hm | = | Vertical distance between Luminaire and workplane |

- Determine the Reflectances of the room floor, walls, and ceiling.
As a guide the following are typical:

| Colour | Reflectance |
| --- | --- |
| White, Off-white, light shades of gray, brown, blue | 75 - 90% |
| Medium green, yellow, brown or grey | 30 - 60% |
| Dark grey, medium blue | 10 - 20% |
| Dark blue, green, wood paneling | 5 - 10% |

Typical values are in the range:

| Ceiling: | 70 – 90% | Walls: | 50 – 70% | Floor: | 20 – 50% |
| --- | --- | --- | --- | --- | --- |

- Once the room index and the room reflectances are decided on the UF can be read off a table similar to the one below. Different tables apply to different luminaires and data should be sought on specific models

| Utilisation Factors (UF) |  |  |  |  |  |  |  |  |  |  |  |  |  | SHR Nom = 2.00 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reflectances |  |  | Room Index (K) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C | W | F | 0.75 |  | 1.00 |  | 1.25 |  | 1.50 |  | 2.00 |  | 2.50 |  | 3.00 | 4.00 | 5.00 |
| 0.70 | 0.50 | 0.20 | 0.31 |  | 0.39 |  | 0.43 |  | 0.46 |  | 0.51 |  | 0.55 |  | 0.57 | 0.61 | 0.63 |
|  | 0.30 |  | 0.25 |  | 0.33 |  | 0.37 |  | 0.41 |  | 0.46 |  | 0.50 |  | 0.53 | 0.57 | 0.60 |
|  | 0.10 |  | 0.21 |  | 0.29 |  | 0.33 |  | 0.36 |  | 0.42 |  | 0.46 |  | 0.49 | 0.54 | 0.57 |
| 0.50 | 0.50 | 0.20 | 0.27 |  | 0.34 |  | 0.37 |  | 0.40 |  | 0.45 |  | 0.48 |  | 0.50 | 0.53 | 0.55 |
|  | 0.30 |  | 0.23 |  | 0.29 |  | 0.33 |  | 0.36 |  | 0.41 |  | 0.44 |  | 0.46 | 0.50 | 0.52 |
|  | 0.10 |  | 0.19 |  | 0.26 |  | 0.29 |  | 0.32 |  | 0.37 |  | 0.41 |  | 0.44 | 0.47 | 0.50 |
| 0.30 | 0.50 | 0.20 | 0.24 |  | 0.30 |  | 0.32 |  | 0.35 |  | 0.39 |  | 0.41 |  | 0.43 | 0.45 | 0.47 |
|  | 0.30 |  | 0.20 |  | 0.26 |  | 0.29 |  | 0.31 |  | 0.36 |  | 0.38 |  | 0.40 | 0.43 | 0.47 |
|  | 0.10 |  | 0.17 |  | 0.23 |  | 0.26 |  | 0.29 |  | 0.33 |  | 0.36 |  | 0.38 | 0.41 | 0.43 |
| 0.00 | 0.00 | 0.00 | 0.13 |  | 0.18 |  | 0.20 |  | 0.22 |  | 0.26 |  | 0.28 |  | 0.30 | 0.32 | 0.34 |

Table 7.4.1 Example Utilization Factors

Based on example, do the followings yourself

## Tutorial 7.4

- A production area in a factory measures 60 metres x 24 metres. Find the number of lamps required if each lamp has a Lighting Design Lumen (LDL) output of 18,000 lumens. The illumination required for the factory area is 200 lux. Utilisation factor = 0.4; Lamp Maintenance Factor = 0.75

- An office area measures (30 x 15) m2, the ceiling to desk height is 2 metres, the area is to be illuminated to a general level of 500 lux using twin lamp 32 watt VDT luminaires with a SHR of 1.25. Each lamp has an initial output of 85 lumens per watt. The maintenance factor has already been determined as 0.636. The supplier has issued the following data with the fittings:

x